| REFERENCE NUMBER: | ERDDF.03.239 |  |
| --- | --- | --- |
| TENDER FOR CIVILs, MECHANICAL, ELCTRICAL, ELV AND FINISHES WORKS FOR THE EXTENSION OF DAR IL-KAPTAN, l-imtarfa for the foundation for respite care services This project is being financed through the European Union Regional Development Fund. IMPORTANT:. - No Bid Bond is requested for this tender.. |
| Date Published: | 8/7/2026 |  |
| Deadline for Submission: | 19/8/2026 | at 09:30am CET/CEST |
| Tender Opening: | 19/8/2026 | At 10:00am CET/CEST |
| DAR IL-KAPTAN Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155, Malta, info@darilkaptan.org, +356 2145 0103/4, +356 7960 5208 |  |  |

Table of Contents

Table of Contents	2

SECTION 1 – INSTRUCTIONS TO TENDERERS	3

1.	3

2. Timetable	4

3. Lots	4

6. Clarification Meeting/Site Visit/Workshop	5

7. Selection and Award Requirements	5

8. Tender Guarantee (Bid bond) ......................................................... 9

9. Criteria for Award	9

SECTION 2 –	11

SECTION 3 – SPECIAL CONDITIONS	13

SECTION 4 –SPECIFICATIONS/TERMS OF REFERENCE (Note 3)	14

SECTION 5 – SUPPLEMENTARY DOCUMENTATION	15

5.1 – Draft Contract Form	15

5.2 – Glossary	15

5.3 – Specimen Performance Guarantee	15

5.4 – Specimen Tender Guarantee (Bid Bond) – where applicable	15

5.4 - Specimen Pre-Financing Guarantee - where applicable ……………………………...15

5.4 - Specimen Retention Guarantee - where applicable ………………………………….. 15

5.4 – General Conditions of Contract	15

Financial Offer / Bill of Quantities	16

Design Documents including Drawings	17

~~~~~~~~~~~~~~~

|  | SECTION 1 – INSTRUCTIONS TO TENDERERS |  |
| --- | --- | --- |
|  | ## 1. General Instructions |  |
| 1.1 | In submitting a tender, the tenderer accepts in full and in its entirety, the content of this tender document, including subsequent Clarifications issued by the Non-Governmental Organisation (NGO), whatever the economic operator’s own corresponding conditions may be, which through the submission of the tender is waived. Tenderers are expected to examine carefully and comply with all instructions, forms, contract provisions and specifications contained in this tender document. These Instructions to Tenderers complement the General Rules Governing Tenders for NGOs. No account can be taken of any reservation in the tender in respect of the procurement documents; any disagreement, contradiction, alteration or deviation shall lead to the tender offer not being considered any further. SUBMISSION OF TENDERS Prospective tenderers must submit their offer by depositing it in the tender box, located at Dar il-Kaptan, Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155. Prospective tenderers take full responsibility to submit their offer by the set tender submission deadline. All tenders must be submitted in one original, clearly marked “original”, and one identical copy (including all documentation as in the original) signed in the same way as the original and clearly marked “copy”, both in hardcopy format. Also tenders must be submitted in an electronic format on a USB and enclosed within the sealed/envelope packages. Both documents and USB are to be separately sealed and placed in another sealed envelope/package so that the bid can be identified as one tender submission. Tenders must be submitted: EITHER by recorded delivery (official postal/courier service) or hand delivered to: Dar il-Kaptan, Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155 Tenders submitted by any other means will not be considered. If the outer envelope is not sealed and marked with the reference number and title of the tender in question, the Non-Governmental Organisation (NGO) will assume no responsibility for the misplacement or premature opening of the tender. Note: Where in this tender document a standard is quoted, it is to be understood that the Contracting Authority will accept equivalent standards. However, it will be the responsibility of the respective bidders to prove that the standards they quoted are equivalent to the standards requested by the Contracting Authority. The Estimated Procurement Value for this Call for Tenders has been based on comprehensive research including appropriate financial analysis. In the context of this procurement, the Estimated Procurement Value, based on market research, is that of € 233,600 excluding VAT. The purpose of this value shall be the guidance of prospective bidders when submitting their offer and is not to be considered as a binding capping price. Therefore, the published Estimated Procurement Value is not restrictive and final on the Contracting Authority. Economic Operators are free to submit financial offers above or below the Estimated Procurement Value. However, the Contracting Authority reserves the right to accept or reject Financial Offers exceeding the Estimated Procurement Value. |  |
| 1.2 | The subject of this tender is the civils, mechanical, electrical, ELV and finishes works for the extension of Dar il-Kaptan, in Mtarfa. |  |
| 1.3 | The place of acceptance of the works shall be Dar il-Kaptan, Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155, the time-limits for the execution of the contract shall be thirty-two (32) calendar weeks from the Order to Start Works, and the INCOTERM2020 applicable shall be Delivery Duty Paid (DDP). |  |
| 1.4 | This is a fee-based contract. |  |
| 1.5 | This call for tenders is being issued under an open procedure. |  |
| 1.6 | The beneficiary of this tender is the Foundation for Respite Care Services. |  |
| 1.7 | This tender is not a reserved contract. |  |
|  | ## 2. Timetable |  |
| 2. | DATE; TIME. Clarification Meeting/Site Visit (Refer to Clause 6.1); 15/7/2026; 9.30AM. Deadline for request for any additional information from the NGO Clarification requests should be addressed to: info@darilkaptan.org; 5/8/2026; 9.30AM. Last date on which additional information can be issued by the NGO; 12/8/2026; 9.30AM. Deadline for submission of tenders (unless otherwise modified in terms of Clause 10.1 of the General Rules Governing Tendering for NGOs); 19/8/2026; 9.30AM. Tender opening session (unless otherwise modified in terms of Clause 10.1 of the General Rules Governing Tendering for NGOs); 19/8/2026; 10.00AM. * All times Central European Time (CET) / Central European Summer Time (CEST) as applicable. |
|  | ## 3. Lots |  |
| 3.1 | This tender is not divided into lots, and tenders must be for the whole of quantities indicated. Tenders will not be accepted for incomplete quantities. The Contracting Authority has considered the division of this contract into lots but has determined that, due to the highly integrated nature of the civil, mechanical, electrical, ELV and finishes works, the project requires a single point of responsibility to ensure effective coordination, clear accountability, and proper sequencing of interdependent activities. Dividing the contract would introduce significant interface risks, increase the likelihood of delays, disputes and health and safety concerns, and place a disproportionate coordination burden on the Authority. Furthermore, given the need for timely delivery of a respite care facility and efficient contract management, a single contract structure is considered the most proportionate and value-for-money approach, while still allowing market access through subcontracting, thereby ensuring compliance with the principles of transparency, non-discrimination and proportionality. |  |
|  | 4. Variant Solutions |  |
| 4.1 | Variant solutions are not permissible. |  |
|  | 5. Financing |  |
| 5.1 | The project is co-financed by the European Union/Government of Malta, in accordance with the rules of the European Regional Development Programme. |  |
| 5.2 | The Contracting Authority of this tender is the Foundation for Respite Care Services. |  |
|  | ## 6. Clarification Meeting/Site Visit |  |
| 6.1 | A clarification meeting/site visit will be held on the date and time indicated in Clause 2, at Dar il-Kaptan, Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155 to answer any questions on the tender document which have been forwarded in writing, or are raised during the same meeting. Minutes will be taken during the meeting, and these (together with any clarifications in response to written requests which are not addressed during the meeting) shall be posted online on the NGOs website as a clarification note as per the General Rules Governing Tendering for NGOs. Meetings between economic operators and the NGO, other than that provided in this clause during the tendering period are not permitted. |  |
|  | ## 7. Selection and Award Requirements |  |
|  | In order to be considered eligible for the award of the contract, economic operators must provide evidence that they meet or exceed certain minimum criteria described hereunder. |  |
|  | (A) Eligibility Criteria Economic Operators are to complete the Eligibility Section through the ESPD (as applicable) and the necessary documents as follows: (Note2) |  |
|  |  | In line with the Construction Industry Licensing Regulations S.L. 623.09 including the amendments ensued via Legal Notices 36 of 2024 and 127 of 2024, Contracts Circular 17/2023 and Contracts Circular 19/2023, Economic Operators shall submit documentation(Note 2) relating to the Service Activity License Application for Construction as detailed hereunder. Economic Operators who applied for the respective Service Activity License/s by the 31st October 2023 and whose application is still being reviewed by the Competent Authority in line with S.L. 623.09, have to submit the Acknowledgement Document of Application Submission which shall indicate at least the: (i) Building and Construction Authority Email Address originating from the System, (ii) Submission Date, (iii) Unique Reference Number which includes the Service Activity License Type, (iv) Identification of the Applicant. (Note 2) Economic Operators who applied for the respective Service Activity License/s as of 1st November 2023 shall submit a Copy of the Provisional Clearance issued by the Competent Authority, namely the Construction Industry Licensing Committee, to continue operating the relevant Service Activity [in line with Regulation 3(5) of S.L. 623.09]. (Note 2) In the eventuality that Economic Operators would already be in receipt of the Service Activity License/s, it is expected that the relevant Economic Operators submit the license Certificate/s in lieu of any other documentation. (Note 2) S.L. 623.09 defines the Provisional Clearance as ‘a clearance issued by the Authority with respect to applications for licence, which clearance shall temporarily authorise the applicant to exercise any of the service activities in respect of which the application relates pending the determination of the application’. |
|  | (i) | Declare agreement, conformity and compliance with the provisions of the Statement on Conditions of Employment by completing the minimum hourly workers’ costs declaration involving the provision of the employees’ services. (Note 2) |
|  | (ii) | Power of Attorney (if applicable) (Note 2) |
|  | (iii) | Information re Joint Venture/Consortium (if applicable) (Note 2) |
|  | (iv) | By submitting an offer, the bidder is confirming that he/she shall provide the Ultimate Beneficiary Owner Sheet upon contract signature. |
|  | (B)(i) Exclusion (including Blacklisting) and Selection Criteria – information to be submitted through the completion of the following declaration forms: |  |
|  | (i) | Declaration concerning exclusion grounds |
|  | (ii) | Declaration concerning Selection Criteria |
|  | (B)(ii) Exclusion (including Blacklisting) and Selection Criteria – information to be submitted through the European Single Procurement Document (ESPD) (Note 2) |  |
|  | (i) | Data Concerning the economic operator to be submitted by filling Part II of the European Single Procurement Document (ESPD). Part II (2A.1 till 2A.13.1) of the ESPD seeks background information about the economic operator. (Note 2) |
|  | (ii) | Part II A Reference 2A.14 till 2A16.6 need only be filled in if the procurement is Reserved. (Note 2) |
|  | (iii) | Part II A Reference 2A.17 till 2A.17.3 need only be filled in when the economic operator is part of a group, consortium, joint venture or similar. (Note 2) Part II A Reference 2A.18 need only be filled where the tender is divided into lots. (Note 2) |
|  | (iv) | Data concerning exclusion grounds to be submitted by filling Part III of the European Single Procurement Document (ESPD). (Note 2) |
|  | (v) | Economic Operators must declare that they meet the minimum criteria established hereunder by filling Part IV of the European Single Procurement Document (ESPD). If no Selection Criteria is requested by the Contracting Authority, the relevant part of the ESPD is to be left blank. (Note 2) a) Suitability (Note 2) Not Applicable b) Financial and Economic Standing(Note 2) Not Applicable c) Technical and Professional Ability(Note 2) Provide data concerning subcontractors and the percentage of works to be subcontracted. This information shall be included in the online ESPD form in Part IV: Selection criteria - Technical and professional ability. Any subcontractor proposed and disclosed at this stage shall be evaluated in line with the Exclusion and Blacklisting Criteria as per these Instructions to Tenderers. Furthermore, if the sub-contractor is relied upon by the Contractor to meet the standards established in the selection criteria, apart from submitting the relevant commitments in writing, such reliance will be evaluated to verify its correctness and whether in effect these criteria are satisfied. It is being understood that if the information being requested regarding sub-contracting is left empty, it will be assumed that no sub-contracting will take place (0% subcontracting). d) Quality Assurance Schemes and Environmental Management Standards(Note 2) Not Applicable |
|  | (vii) Concluding statements to be submitted by filling Part VI of the European Single Procurement Document (ESPD). (Note 2) |  |
|  | (C) Technical Specifications |  |
|  | (i) | Tenderer’s Technical Offer in response to specifications. (Note 3) The Tenderer’s Technical Offer shall constitute the following: - The Technical Questionnaire (Note 3) - Key Experts Form, the Statement of Availability Form, the Self-declaration form for Key Experts (relating to public employees) and CVs (Note 2) The following key experts shall be employed by the Contractor for the duration of the works: - Key Expert 1: Contractor’s Perit - Key Expert 2: A Site Manager N.B. Further details on the qualification and experience of the Key Experts proposed by the Contractor may be found in Section 4 – Technical Specifications. |
|  | (ii) | Literature as per Form marked ‘Literature List’ to be submitted with the Technical offer at tendering stage. Alternatively, an Economic Operator can quote a reference number under which he/she has already supplied items so that there would be no need to submit literature. (Note 2) |
|  | (D) Financial Offer |  |
|  | (i) | The Tender Form and Tenderer’s Declaration are to completed and submitted with the offer.(Note 3) |
|  | (ii) | A financial offer is to be submitted by filling in Bill of Quantities, and is to be calculated on the basis of Delivered Duty Paid (DDP)2020 (Grand Total) for the works tendered. (Note 3) |
|  | Notes to Clause 7: 1. Tenderers will be requested to clarify/rectify, within five (5) working days from notification, the tender guarantee only in the following four circumstances: incorrect validity date, and/or incorrect value, and/or incorrect addressee and incorrect name of the bidder. Rectification in respect of the Tender Guarantee (Bid Bond) is free of charge. 2. Tenderers will be requested to either clarify/rectify any incorrect and/or incomplete documentation, and/or submit any missing documents within five (5) working days from notification. 3. No rectification shall be allowed. Only clarifications on the submitted information may be requested. Request for Clarification and / or rectifications concerning a previous request dealing with the same shortcoming shall not be entertained. |  |
|  | 8. Tender Guarantee (Bid bond) |  |
| 8.1 | No tender guarantee (bid bond) is required. |  |
|  | ## 9. Criteria for Award |  |
| 9.1 | The sole award criterion will be the price. The contract will be awarded to the tenderer submitting the cheapest priced offer satisfying the administrative and technical criteria. |  |

SECTION 2 – EXTRACTS FROM THE PUBLIC PROCUREMENT REGULATIONS

Part IX of the Public Procurement Regulations – S.L. 601.03

Appeals from decisions taken after the closing date for the submissions of an offer (applicable to procurement where the estimated value meets or exceeds Euro5K)

270. Where the estimated value of the public contract meets or exceeds five thousand euro (€5,000) any tenderer or candidate concerned, or any person, having or having had an interest or who has been harmed or risks being harmed by an alleged infringement or by any decision taken including a proposed award in obtaining a contract, a rejection of a tender or a cancellation of a call for tender after the lapse of the publication period, may file an appeal by means of an objection before the Public Contracts Review Board, which shall contain in a very clear manner the reasons for their complaints.

271. The objection shall be filed within ten (10) calendar days following the date on which the contracting authority or the authority responsible for the tendering process has by fax or other electronic means sent its proposed award decision or the rejection of a tender or the cancellation of the call for tenders after the lapse of the publication period.

272. The communication to each tenderer or candidate concerned of the proposed award or of the cancellation of the call for tenders shall be accompanied by a summary of the relevant reasons relating to the rejection of the tender as set out in regulation 242 or the reasons why the call for tenders is being cancelled after the lapse of the publication period, and by a precise statement of the exact standstill period.

273. The objection shall only be valid if accompanied by a deposit equivalent to 0.50 per cent of the estimated value set by the contracting authority of the whole tender or if the tender is divided into lots according to the estimated value of the tender set by the contracting authority for each lot submitted by the tenderer, provided that in no case shall the deposit be less than four hundred euro (€400) or more than fifty thousand euro (€50,000) which may be refunded as the Public Contracts Review Board may decide in its decision.

274. The Secretary of the Public Contracts Review Board shall immediately notify the Director, the Sectoral Procurement Directorate and, or the contracting authority, as the case may be, that an objection had been filed with his authority thereby immediately suspending the award procedure.

275. The Department of Contracts, the Sectoral Procurement Directorate or the contracting authority involved, as the case may be, shall be precluded from concluding the contract during the period of ten (10) calendar days allowed for the submission of appeals. The award process shall be completely suspended if an appeal is eventually submitted.

276. The procedure to be followed in submitting and determining appeals as well as the conditions under which such appeals may be filed shall be the following:

(a) any decision by the General Contracts Committee, the Sectoral Procurement Directorate or the Special Contracts Committee or by the contracting authority, shall be made public by affixing it to the notice-board of the Department of Contracts, the Sectoral Procurement Directorate or of the office of the contracting authority, as the case may be, or by uploading it on government’s e-procurement platform prior to the award of the contract if the call for tenders is administered by the Department of Contracts;

(b) the appeal of the complainant shall also be affixed to the notice-board of the Public Contracts Review Board and shall be communicated by fax or by other electronic means to all participating tenderers;

(c) the contracting authority and any interested party may, within ten (10) calendar days from the day on which the appeal is affixed to the notice board of the Review Board and uploaded where applicable on the government’s e-procurement platform, file a written reply to the appeal. These replies shall also be affixed to the notice board of the Review Board and where applicable they shall also be uploaded on the government’s eProcurement platform;

(d) the authority responsible for the tendering process shall within ten (10) days forward to the chairman of the Public Contracts Review Board all documentation pertaining to the call for tenders in question including files and tenders submitted;

(e) the secretary of the Review Board shall inform all the participants of the call for tenders, the Department of Contracts, the Sectoral Procurement Directorate and the contracting authority of the date or dates, as the case may be, when the appeal will be heard;

(f) when the oral hearing is concluded, the Public Contracts Review Board, if it does not deliver the decision on the same day, shall reserve decision for the earliest possible date to be fixed for the purpose, but not later than six (6) weeks from the day of the oral hearing:

Provided that for serious and justified reasons expressed in writing by means of an order notified to all the parties, the Public Contracts Review Board may postpone the judgment for a later period;

(g) the secretary of the Review Board shall keep a record of the grounds of each adjournment and of everything done in each sitting;

(h) after evaluating all the evidence and after considering all submissions put forward by the parties, the Public Contracts Review Board shall decide whether to accede or reject the appeal or even cancel the call if it appears to it that this is best in the circumstances of the case.

SECTION 3 – SPECIAL CONDITIONS

|  | These conditions amplify and supplement, if necessary, the General Conditions governing the contract. Unless the Special Conditions provide otherwise, those General Conditions remain fully applicable. The numbering of the Articles of the Special Conditions is not consecutive but follows the numbering of the Articles of the General Conditions. Other Special Conditions may be indicated afterwards. |
| --- | --- |
|  | ### Article 4: Communications |
| 4.1 | Further to the provisions in the General Conditions, all communications at tendering stage shall be done through info@darilkaptan.org ONLY. Following award of contract, any communication (including invoicing) should be made with: Address:; DAR IL-KAPTAN Rotary Drive Triq il-Kaptan, Mtarfa MTF 1155, Malta,. Email:; info@darilkaptan.org. Further to the provisions of the General Conditions, full details of the Contracting Authority’s appointed (CA) Supervisor and of its representatives and/or the Architect in Charge, shall be notified to the appointed Contractor together with the Order to Start Works. Upon receipt of Order to Start Works, the Contractor shall notify the Contracting Authority’s Supervisor or his/her representative with the details of the Contractor’s Key Experts engaged in the project. These details are to include a mobile phone number that is accessible during office hours for the duration of project and a regularly checked email address of the aforementioned Contractor’s Key Experts. |
| 4.3 | Further to the provisions of the General Conditions, unless otherwise agreed to in writing, following award of the contract, communication between the Contractor and the Contracting Authority shall be between each entity’s representative, namely the CA Supervisor and/or representative appointed by the Contracting Authority and/or AiC and the Contractor’s Perit. Each party shall have the right to change the appointed representative through the course of the contract subject to written notification to the other party. |
|  | ### Article 5: Supervisor and Supervisor's Representative |
| 5.1 | Further to the provisions of the General Conditions, the Contractor’s Perit shall receive, on behalf of the Contractor, instructions related to any part of the works. These instructions shall be deemed to have been given to the Contractor and therefore will be immediately acted upon. The Contractor shall notify the Contracting Authority with any applicable modifications to the contract, prior to execution of such instructions. |
| 5.4 | Administrative orders, site instructions and/or orders will be delivered by email. |
| 5.5 | Further to the provisions of the General Conditions, the CA Supervisor and / or representative and / or AiC shall have the power during the course of the work, to order the Contractor to halt all works and/or remove from the work site any materials, equipment, or supplies that are considered to be of an inferior quality. He/she shall also have the power to order the removal and the replacement and/or proper re-execution of any work or materials in question that is deemed inferior or contrary to the quality / technical specifications stipulated within this contract. Any such orders concerning replacement and/or re-execution shall be carried out by the Contractor at his / her own expense. In case the Contractor fails to carry out such orders, the CA Supervisor and / or representative from the Contracting Authority and/or AiC, shall have the power to employ and pay other persons to carry out the same works at the Contractor’s expense; such expenses will be deducted from any monies that may be due to the Contractor. Should it appear to the CA Supervisor and / or representative, or any duly authorised member of his/her staff, that any work in progress is being executed in a faulty or defective manner, with unsuitable materials, by unskilled workmen and/or by any means or manner not in accordance with the contract documents, then he/she/they may order immediate suspension of such faulty or defective works to the Contractor’s Key Experts, until such time as the Contractor shall adopt remedial measures to the satisfaction of the CA Supervisor and / or representative. Such order shall be complied with immediately. The Contractor shall not be entitled to any extra payment, compensation or extension of time for the completion on account of such suspension. |
|  | ### Article 8: Supply of Documents |
| 8.1 | Within thirty (30) calendar days of the signing of the contract and upon the request by the Contractor, the CA Supervisor and / or representative shall provide the Contractor, free of charge, with a soft-copy of any contract documents prepared for the performance of the contract. |
| 8.4 | The procedure used by the Contracting Authority and the CA Supervisor and / or representative to approve drawings and other documents provided by the Contractor shall be as indicated in the Technical Specifications. |
|  | ### Article 10: Assistance with Local Regulations |
| 10.1 | It is the Contractor’s responsibility to conform and comply with all applicable National and EU Legislation, regulations, standards and codes of practice, and to obtain necessary permits, visas, authorisation or licences required to perform the contract. Any applicable fees required to enable full execution of the works in this contract shall be borne by the Contractor. |
| 10.5 | The Contractor is reminded of the obligation to declare direct imports and exports from the EU if applicable. |
|  | ### Article 11: The Contractor’s Obligations |
| 11.1 | Further to the provisions of the General Conditions, the Contractor’s Perit will be fully and solely responsible for the supervision of the Works. The Contractor’s Perit will be required to render his services during all project phases. Furthermore, the Contractor is responsible and liable for all materials and items collected from the Contracting Authority, even those already laid in the works, until the full contract is completed and taken over by the Contracting Authority. Should any items and/or material supplied by the Contracting Authority to the Contractor go missing, are stolen or otherwise are not utilised in the works as specified and directed by the appointed CA Supervisor and / or representative, and if they are not duly returned to the Contracting Authority’s stores in their original condition, the Contractor will be held responsible and liable for the value that the Contracting Authority may establish towards their cost. This amount shall be deducted from any amounts due under this contract or from any retention money as the Contracting Authority may deem appropriate. During execution of works, the Contactor shall, at all times, have at least one person on site who can communicate fluently in Maltese and/or English. |
| 11.4 | Further to the provisions of the General Conditions, the Contractor will not be able to change any appointed Key Expert without the prior approval of the Contracting Authority. In the event that any Key Expert shall be absenting himself from the performance of his duties for any length of time, the Contractor must indicate the name of a substitute Key Expert with the same requisites as established in the tender document, to be approved by the Contracting Authority, to replace him/her during his/her absence. The Contracting Authority may request the Contractor to change the Key expert should the latter fails to fulfil its duties as specified in the technical specifications. The Contractor shall provide a suitable replacement within two weeks for the notification by the Contracting Authority (CA). |
| 11.6 | The equipment, which the Contractor has on site, shall be deemed to be for the purpose of carrying out the works as outlined within the applicable method statements and health and safety plan. The Contractor shall have in its possession any applicable equipment certification and shall be provided to the CA Supervisor and/or representative upon request. |
| 11.8 | Without prejudice to Article 35, the Contractor shall comply fully with any administrative orders given to him. Where the Contractor considers that the requirements of an administrative order exceed the authority of the CA Supervisor and / or representative and / or AiC or the scope of the contract, he shall, on pain of being time-barred, notify the CA Supervisor and / or representative of this fact within two (2) working days of receiving the administrative order and inform the Contracting Authority. Execution of the administrative order shall be suspended during this period. Following the issue of an administrative order by the CA Supervisor and / or representative and / or AiC, the Contractor shall execute the administrative order within the deadline specified for the execution of the respective administrative order. Without prejudice to other penalties which may be due in terms of the Contract, if the Contractor fails to respect the specified deadline, Contractor shall be liable to a penalty of 0.1% of the Contract value per calendar day of mere delay, until CA Supervisor and / or representative certifies the completion of the administrative order, which penalty shall be deducted from the next interim payment / final payment. |
| 11.11 | Following the award of the Contract and during its implementation, the Contractor shall be required to prepare the following basic documents (as and when required) for the approval of the CA Supervisor and / or representative (and other Local Authorities). Should the CA Supervisor and/or representative consider any alteration or addition to the submittals and reports mentioned below, as submitted in their last version, the Contractor shall conform therewith without additional costs to the Contracting Authority. The submission to and approval by the CA Supervisor and/or representative of such documents shall not relieve the Contractor of any of his duties or responsibilities under the Contract. The Contractor is bound to provide any revisions to the documents as requested by the Contracting Authority. Where a date is not specified, the Contractor shall provide the requested updated documentation within five (5) working days. The Contracting Authority shall become the owner of these documents, upon submittal by the Contractor, and may be reproduced or used for another purpose, and communicated to third parties, without the consent of the Contractor. The below list shall not be considered as an exhaustive list and other reports may be requested as required for completion of the works. Table 1: Schedule of the basic contract documents to be approved by the contracting authority Document; Date of Submittal; Signed by. Inception Report - Programme of Works - Construction Management Plan - Works Method Statements - Photographic Survey - H&S Risk Assessment - Condition Reports - Quality Assurance and Control Plan; Three (3) weeks from Contract signing; Contractor’s Perit. QA reports; Every month and before interim payments; QA provider & Contractor’s Perit. Monthly Progress Reports; Every month; Contractor’s Perit. Designs, Drawings and Manuals; Fifteen (15) calendar days upon request by the CA; Contractor’s Perit. Final Report; Four (4) weeks from the date of Partial Provisional Acceptance; Contractor’s Perit. |
|  | - Inception Report |
|  | - Programme of Works |
|  | - Following award of the Contract, a meeting shall be held between the Contractor and the CA supervisor and/or representatives to discuss any specific time issues. The Contractor shall provide an updated detailed Programme of Works, reflecting the decisions taken during this meeting. - Refer to Article 15 of these conditions for more details about the Programme of Works. |
|  | - Construction Management Plan |
|  | - Where applicable, before commencing the Works, the Contractor shall provide a comprehensive Construction Management Plan (CMP) to partially fulfill the requirements of the Planning Authority (PA) Permit and the terms of reference set by the Environmental Resources Authority (ERA). The Contracting Authority will review and approve the CMP. |
|  | - Contractor’s Method Statement |
|  | - Prior to the start of the Works the Contractor’s Perit shall submit detailed Works Method Statements of each major activity whether directly controlled or subcontracted. The Works Method Statements shall be subject to review and approval of the AiC on behalf of the Contracting Authority. Method Statements for BCA approvals are to be prepared on a when required basis. - In the preparation and implementation of all Method Statements, the Contractor shall be fully responsible for ensuring that the ongoing operations of Dar il-Kaptan are not disrupted, hindered or adversely affected in any manner whatsoever throughout the execution of the Works. To this end, the Contractor shall clearly set out, within each Method Statement, a detailed Operational Continuity Plan identifying: - the sequencing of works in proximity to operational areas; - the physical segregation measures to be implemented (including hoardings, barricades, controlled access routes, and signage); - arrangements for maintaining safe and uninterrupted access for staff, residents/clients and visitors at all times; - contingency measures to address unforeseen disruptions or emergencies. - The Contractor shall adopt a proactive mitigation approach and shall incorporate in the Method Statements all necessary preventive and control measures to minimise nuisance and disturbance. Without prejudice to the generality of the foregoing, such measures shall include: - the implementation of effective dust suppression systems; - the use of noise control and attenuation measures; - the management of vibrations, odours, and other environmental impacts that may affect the facility. - Particular consideration shall be given to the sensitive nature of the facility, and the Contractor shall ensure that all operations are carried out with due care, professionalism and respect for users of the premises, including vulnerable persons. - Failure to adequately safeguard ongoing operations or to implement the prescribed mitigation measures shall be deemed a material breach of contract, without prejudice to any instructions that may be issued by the AiC, including suspension of works, imposition of remedial measures at the Contractor’s cost, or application of contractual penalties where applicable |
|  | - Photographic Survey |
|  | - A photographic survey of the entire site (within the contract limits) shall be undertaken. All structures and items of relevance to be cleared shall be photographed. All photographs are to be dated and referenced on a plan. |
|  | - Monthly Progress Report |
|  | - The Contractor shall submit to the CA Supervisor and/or representative a Monthly Progress Report on the last working day of each month or as and when requested by the Supervisor and/or representative. It shall include - Summary of works carried out - Any issues and risks to be highlighted - Cost controls - Any expected modifications - Updates on Progress meetings - Quality of Work - H&S reports including updates to the risk assessment. - The OHSO is responsible to keep track and prepare the Risk Assessment prior to the commencement of respective activities. - Photographic evidence of the progress of work, - The Contractor shall provide high-definition progress photographic and video records showing different stages of the Works. He shall also provide additional records as the CA Supervisor and/or representative may indicate. All such record material shall contain references to the location and type of the actual site of works to monitor effectively the progress and recording of the works. The CA Supervisor and / or representative will not accept such records unless these are referenced clearly and properly. - The electronic files of progress photographic shall be supplied to the CA Supervisor and / or representative on a weekly basis as part of the monthly report. - Tracked programme of work clearly showing progress and off-set from approved PoW. - The Contractor shall agree with the CA Supervisor and/or representative on modifications and detailing of the report structure and format, which shall be modified from time to time as deemed necessary by the CA Supervisor and / or representative. - Acceptance of the Monthly Progress Report does not constitute the explicit Contracting Authority’s Agreement to any document included in the list above. |
| 11.14 | The contractor binds himself to adhere to the drawings, document and conditions imposed in Planning Permit as will be approved by the Planning Authority. |
|  | ### Article 12: Superintendence of the Works |
| 12.1 | Further to the provisions of the General Conditions, the Contractor’s Key Experts shall receive on behalf of the Contractor, instructions related to any part of the works. These instructions shall be deemed to have been given to the Contractor and therefore will immediately be acted upon. |
|  | Article 13: Performance Guarantee |
| 13.1 | The Contractor shall, within fifteen (15) calendar days of receipt of the contract, sign and date the contract and return it together with a copy of the Performance Guarantee. The copy of the Performance Guarantee shall be forwarded to the Contracting Authority. The contract will not be endorsed by the Contracting Authority until the performance guarantee is submitted. The Contractor is therefore obliged to forward the original Performance Guarantee to the Contracting Authority. The amount of the guarantee shall be 4% of the total contract value. |
| 13.2 | Not applicable. |
| 13.3 | The Contractor has the possibility to provide the Contracting Authority with a Single Bond covering two (2) or more Contract Agreements (that qualify for a performance guarantee) with the same Contracting Authority. If an additional contract is awarded to a given Contractor, which results in an economic operator’s current cumulative contracts value to go beyond the contract value range currently covered by the Single Bond, the Contractor is to be requested to; either submit a separate Performance Guarantee for the additional contract; or else submit a new Single Bond to cover the new total contracts value or submit an amendment to the original Single Bond specifying the new amount. If a Contractor opts to make use of a Single Bond, one must submit an endorsed and signed letter from the respective Contracting Authority / Entity specifying which contracts shall be covered by the said Single Bond. The letter would need to be resubmitted should a new Contract Agreement be covered by the Single Bond. The same process shall take place if a Contract Agreement no longer forms part of the Single Bond since the Contract would have been fully implemented and executed. In addition, if the inclusion of a new Contract Value does not affect the current amount of the Single Bond because the applicable Cumulative Contracts Value Range would not have been exceeded, the letter would need to specify this accordingly. In absence of the said letter, the new Contract Agreement would not be signed (in line Procurement Policy Notes 21 and 22). |
| 13.5 | The performance guarantee shall be in the format given in Section 4 and shall be provided in the form of a bank guarantee. It shall be issued by a bank in accordance with the eligibility criteria applicable for the award of the contract. |
| 13.9 | The performance guarantee shall be released within thirty (30) days after the issuing of the Provisional acceptance certificate. Prior to the release of the Performance Guarantee the Contractor is to submit a Retention Guarantee amounting to 5% of the total contract value. The Retention Guarantee shall be released upon Final Acceptance as per Article 59 of the Special Conditions. |
|  | ### Article 14: Insurance |
| 14.1 | Further to the provisions of the General Conditions, the Contractor shall take out a Contractor’s All Risk Insurance Policy in his own name and including Subcontractors and/or the Contracting Authority and/or other Contractors and/or the CA Supervisor and / or representative against any loss or damage for which he is liable under the contract. Insurance cover is to be endorsed by means of a cross-liability clause to the effect that it shall cover claims made by the Contracting Authority notwithstanding that the said policy is also in their name. Such insurance shall cover: - The works together with materials and plant for incorporation therein, to the full replacement cost against loss or damage arising from an insurable cause. - An additional sum of 20% of such replacement cost, to cover all the additional direct or indirect costs incurred for professional fees and debris removal following loss or damage. - The Contractor’s Plant and Machinery brought onto the site by the Contractor, for a sum sufficient to provide their replacement at the site. - Liability for injuries and damages to third parties and third-party property for an amount of not less than €750,000. Provided that the Contractor shall carry out an appropriate and adequate assessment of the risks involved and if the said value of €750,000 is not considered sufficient, the Contractor shall ensure that such coverage is duly increased. - The Insurance period shall start from the commencement of the works until the issuance of the Provisional Acceptance Certificate. - This Policy shall cover Principal Own Surrounding Property and workmen on site. - Completed operations Liability Insurance – Covering third party damages caused by the works that occur after the Contractor completes the job and usually starts from date of hand over and renewable for five (5) years. |
| 14.3 | Further to the provisions of the General Conditions, Warranted Key Experts must be covered by a Professional Indemnity Insurance to cover all aspects of their professional practice having a minimum limit of € 1,000,000 per occurrence. The definition of the Insured shall include the Principal of the Policyholder and any other consultants, self-employed, sub-Contractors solely under contract or under direct supervision of the Policyholder. This Policy which shall be maintained for the whole period of professional liability as defined under the laws of Malta. |
| 14.4 | Further to the provisions of the General Conditions, all insurances referred to in Article 14 shall also be applicable to the Contractor with respect to the Subcontractors. |
| 14.5 | All the insurance referred to in this Article shall be taken out within three (3) calendar weeks, from signing of contract and shall be subject to approval by the Contracting Authority. Such insurance shall take effect as from the commencement of the works and remain in force until final acceptance of the works. The Contractor shall present the Contracting Authority with a certified true copy of the insurance policy and proof that premiums have been duly paid. This clause shall not imply any responsibility on the Contracting Authority should the Contractor fail to provide such proof and shall remain solely responsible for the provision of such cover. The premium/s shall be affected by the Contractor at his own expense. The insurances shall for all effects and purposes be deemed to be a Maltese Contract and shall be governed according to the Maltese Laws and subject to the Maltese Courts jurisdiction. Each time the premium is paid, the Contractor shall submit evidence of payment to the Contracting Authority. |
| 14.6 | If and in so far, the Contractor fails to effect and keep in force any of the insurance policies referred to in Article 14 of these Conditions of Contract, then the Contracting Authority may effect and keep in force any such insurance and pay any premium as may be necessary for that purpose and deduct the amount so paid from any monies due to the Contractor. |
| 14.7 | Further to the provisions of the General Conditions, any amounts not insured or not recovered from the insurers shall be borne by the Contractor. In the event that the Contractor fails to comply with conditions imposed by the insurance policies effected pursuant to the contract, he shall indemnify, hold harmless the Contracting Authority and waive all subrogation rights against all losses and claims (including but not limited to costs incurred/claims made by third parties for loss in business or delays in provision of services) arising from such failure. The insurances referred to in Article 14 in these Conditions of Contract shall be affected with insurers to the satisfaction of the Contracting Authority and the Contractor shall be deemed to be aware of the terms and conditions thereof. The Contractor shall, with all due diligence, conform to the terms and conditions of such insurances (including conditions, instructions and procedures as laid down in the contract and the Insurance Brochure, Claims Procedures and Insurance Contract Conditions of all insurance policies resulting from the contract) and all reasonable requirements of insurers in connection with the prosecution and settlement of claims, the recovery of losses and the prevention of accidents and shall bear at his own cost the consequences of any failure to comply. The Contractor shall bear the cost of all excesses (deductibles), exclusions or limitations applying under the said policies (in so far as these concern risks for which he is responsible under the terms of the contract) whether in respect of claims made against the Contractor and/or the Authority and/or the CA Supervisor and / or representative pursuant to the provisions of any enactment. If the Provider fails to insure, as he is so bound to do under this contract, he shall be personally responsible for any damages arising. Subject that, when the Contracting Authority finds out about such default it shall give the Contractor a period of a week to regularize his position, failure of which the Contracting Authority will ipso jure terminate the Contract and appoint others to complete the works. It shall be the sole responsibility of the Provider to make adequate provisions for the taking out of any additional insurance in respect of plant, employees and the works in general as he may deem appropriate. |
| 14.8 | Further to the provisions of the General Conditions, the Contractor shall notify the insurers of changes in the quantum, nature, extend and programme for the extension of the Project and ensure the adequacy of the insurance at all times in accordance with the terms of the contract. |
| 14.9 | The Contractor shall cover up and protect from damage from any cause, the works under the contract/s awarded to him. He must supply protection for the whole works executed, and any damage caused shall be made good by the Contractor at his own expense. The Contractor shall take all precautionary measures as may be necessary for the protection of persons and property for the proper execution of the Works to satisfy the regulatory requirements of the Planning Authority, the Environment and Resources Authority the Occupational Health and Safety Unit, the Building Construction Agency or any other Authority or Department. The Contractor’s insurance shall fulfil any and all insurance requirements specified in LN 136 of 2019 or any revision thereof. |
|  | ### Article 15: Performance Programme (Timetable) |
| 15.2 | Following award of the Contract, the Contractor shall provide an updated detailed Programme of Works in the form of a Gantt Chart, as per Article 11.11(A)(i) of these conditions. Where requested by the CA Supervisor and/or representative, the Contractor shall provide, at no additional cost, a programme of works using an approved Project Management Software Programme and produced as a result of a ‘critical path analysis’. The Programme must abide by the constraints indicated below. It shall show the necessary level of detail appropriate to each stage of the Works and all activities and constraints, each of which shall be given a short descriptive title. All events shall be numbered and annotated with the earliest and latest event dates. The Programme of Works shall be such as to allow the Contractor and Contracting Authority to accurately measure the progress of the Works in real time and must: - Set milestones (incl BCA documentation) - Define the Work Tasks and assign in manageable components - Define the links, relationships and critical paths - Identify the dependencies - Estimate the Durations - Assign monitoring and controls - Quantify and assign the Resource Requirements (Materials, HR and Plant) for Work Activities |
| 15.3 | Further to the provisions of the General Conditions, the CA Supervisor and / or representative shall, whenever changes occur and/or it is deemed necessary, instruct the Contractor to update the Programme of Works further, and distribute copies to all parties. |
| 15.4 | Where the Contractor updates the Programme of Works, approval of an updated Programme of Works does not directly lead to an Extension of Contract Performance. Extension of Time shall be covered by a separate approval. |
| 15.5 | The Contractor shall be liable to a penalty of €200.00 per day up to a limit of 10% of the total contract price for each calendar day in which it fails to submit the detailed Programme of works as requested in the provisions of Clause 15.3 above. |
|  | ### Article 17: Contractor’s Drawings/Diagrams |
| 17.1 | Further to the provisions of the General Conditions, the Contractor shall prepare and submit the following documents as described below and as per Table 1 of Article 11.11 of these conditions. |
|  | Designs, Drawings and Manuals |
|  | - The Contractor’s Perit, together with the other Key Experts/ Other Experts, shall prepare, endorse and submit the below list of designs and drawings, specifications and manuals for the approval of the Contracting Authority; - Working drawings/Shop Drawings of works as necessary. - Other drawings required for Design & Build structures. - Drawings for the set-up of payment claims and financial modifications. - As-built detailed drawings including levels, dimensions, layout of services, civil works, structural drawings, finishes, etc. - Any drawings required for the completion of works upon Contracting Authority’s request. - Specifications, samples and manuals (as applicable) - Before the commencement of works, where applicable, the Contractor shall submit the relevant designs and drawings to the CA Supervisor and / or representative for review and approval. - All drawings shall be provided to the Contracting Authority in both PDF and CAD versions. - The approval of the Contracting Authority on the drawings does not exonerate the Contractor from any of his responsibilities on the submissions. The approval of the Contracting Authority shall only provide an administrative approval and the responsibility of the correctness and integrity of such drawings remain with the Contractor. - Standard metric scales shall be used for all drawings, unless otherwise requested by the CA Supervisor and/or representative. The scale ratio and a corresponding metric scale bar shall be clearly and legibly indicated on the same sheet (or, where drawings at different scales are included on the same sheet, under the corresponding drawing). Drawings shall not be reduced to fit, as it may distort or affect the scale or the drawing itself. |
| 17.7 | Further to the provisions of the General Conditions, the language to be used when submitting manuals, drawings and any other documents shall be the English language. |
|  | Article 18: Sufficiency of Tender Prices |
| 18.1 | The Contractor shall be deemed to have taken into account in his tender price all works that are necessary to complete the project and to fully hand over in operational condition. |
| 18.2 | Further to the provisions of the General Conditions, no claims whatsoever, for extra costs due to possible omissions in the Contractor’s tender, shall be entertained by the Contracting Authority. The Contractor shall also be deemed to have factored in his prices any possible change in prices, rates and/or fees payable by the Contractor to third parties. Any claims related to such changes shall not be entertained by the Contracting Authority. |
|  | Article 20: Safety on Site |
| 20.2 | Further to the provisions of the General Conditions, it is the obligation of Contractors to carry out a suitable, sufficient and systematic assessment of all the occupational health and safety hazards which may be present at the place of work and the resultant risks involved concerning all aspects of the work activity. The Contractor shall take all possible measures to ensure maximum safety for his workers and for all persons who may be within the premises during the contract period. Danger areas are to be cordoned off unless impracticable. The Contractor shall comply with the latest Health and Safety regulations as issued by the Occupational Health and Safety Authority (OHSA) with regards to safety wear for the employees and shall install temporary warning signs of ongoing works. All precautions are to be taken by the Contractor to eliminate danger to the public and to the workmen. All damages to any private or public property around the project site and/or injuries to persons sustained during the execution of the works shall be the responsibility of the Contractor. Furthermore, the Contractor shall provide and maintain all necessary first aid kits and sanitary facilities that are to be made available to any workers throughout the duration of the works. |
| 20.3 | Further to the provisions of the General Conditions, it is also the duty of the Contractor to cooperate with other employers, Contractors and, or self-employed persons who share a common workplace, on the implementation of Health and Safety provisions. The Contractor or his/her designate shall co-ordinate necessary actions in matters which concern protective and preventive measures and shall inform all on site as well as the CA Supervisor and / or representative regarding any potential risks. |
| 20.6 | The Contractor shall, at its sole expense, provide temporary lighting when and as required throughout the execution of the Work. |
| 20.7 | The Contractor shall have a formal health and safety management system that ensures the creation of project health and safety plans in order to achieve the requirements of statutory dispositions set out in Chapter 646 of the Laws of Malta (Occupational Health and Safety Authority Act), as well as any other national legislation, regulations, standards, and/or codes of practice regarding health and safety issues, in effect during the execution of the contract, as they may apply for the Contractor’s particular operating situation and nature of work activities. |
| 20.8 | The Contractor shall appoint a competent occupational health and safety officer (OHSO) in line with the requirements set out in the Key Experts’ Form and with an acquired level of knowledge as stipulated in the terms of Chapter 646. The OHSO shall, for the duration of the works, represent the Contractor on all matters relating to health and safety. The OHSO shall remain accountable to the health and safety supervisor appointed by the Contracting Authority. |
| 20.9 | Amongst the generality of its duties, the OHSO shall abide to any and all directions as shall be given by the CA Supervisor and / or representative and/or AiC and in so doing, shall co-ordinate and monitor the site works in line with health and safety statutory requirements. In particular, the OHSO shall ensure that the Contractor acts in full compliance with health and safety standards and legislation, and/or any such directions as may be given by the health and safety supervisor appointed by the Contracting Authority. |
| 20.10 | The Contractor shall be liable to the Penalties, in accordance with Article 11.8 of these Special Conditions of Contract, for each and every day of delay following the set deadline for addressing any issues resulting from non-conformity in relation to provisions of Article 20 of the General Conditions of Contract and Special Conditions. |
| 20.11 | Furthermore, should the Contractor fail to abide by the corrective action specified in the Health and Safety requirements of the site visit report within the specified deadline, he/she shall be informed in writing by the CA Supervisor and / or representative with the aggregate amount of penalties that will be deducted from the next interim payment. The amount of such penalties will be calculated as five hundred euro (€500) for each health and safety site visit report that reveals infringement/s from the Health and Safety requirements. If the Contracting Authority deems that proper action is to be taken immediately and the Contractor fails to take the required steps to implement such instructions within the prescribed time, the Contracting Authority, without need of giving further notice to the Contractor, shall be free to carry out such steps itself or appoint third parties to carry out such instructions at the defaulting Contractor's expense. |
|  | Article 21: Safeguarding adjacent Properties |
| 21.3 | Further to the provisions of the General Conditions, the Contractor shall prepare and submit the following documents as described below and as per Table 1 of Article 11.11 of these conditions. |
|  | Condition Reports |
|  | - The Contractor is responsible to carry out condition reports to third party properties or other structures contingent to the works as directed by the Contractor’s Perit. The Condition Reports needs to be endorsed by the Contractor’s Perit, Insurance and BCA (when required). The reports are to be submitted prior to the commencement of works. The Contractor is responsible to inform and agree on the date of the site inspection for the set-up of the Condition Report with the Contracting Authority at least three (3) working days before the site inspection. |
|  | ### Article 24: Setting-Out |
| 24.4 | Further to the provisions of the General Conditions, the Contractor is responsible for all levels and setting out of the works. Any surveys submitted by the Contracting Authority is for guidance purposes only. The Contractor is responsible to carry his own survey before the commencement of the works, during works and upon works completion. The Contracting Authority shall instruct the Contractor to carry further surveying services during the course of works which may be necessary for the completion of the works. The Contractor’s Perit must check and endorse the surveys which needs to be submitted to the Contracting Authority. All significant changes between the survey shown on the Contract drawings and the Contractor’s survey are to be immediately notified to the Contracting Authority. The Contractor shall be responsible for the necessary setting out of all the works. The Contractor shall inform the CA Supervisor and/or representative of the dates when the surveying and setting out processes will take place. The Contractor shall also set out any excavations to the required depth and profile. The cost of the Surveying services are deemed as already included in the rates. The Contractor shall liaise with the relevant authorities to obtain benchmark, levels, building alignments and other. |
|  | ### Article 31: Commencement Date |
| 31.1 | The Contracting Authority shall issue an order to start works. The contract commencement date shall be as stipulated in the order to start works. The order to start works will be issued within eight (8) weeks from last signature of the contract. Failure to mobilise on site and commence works as programmed and confirmed in the commencement order shall be considered as delay in commencement and will render the Contractor liable to the same penalties indicated in Article 34. |
|  | ### Article 32: Period of Execution of Tasks |
| 32.1 | The performance period of the Contract shall be thirty-two (32) calendar weeks from the Commencement Date indicated on the Order to Start Works. |
|  | ### Article 34: Delays in Execution |
| 34.1 | The daily penalty rate in Euro for any delay in performance from the approved programme of works of the contract shall be calculated for in relation to the contract value and execution period of the contract by using the following calculation: 0.1% of the Contract value per calendar day of mere delay. Example: Contract Value; Completed % of PoW; % of PoW delayed; Applicable Penalties. €100,000; 50%; 50%; 0.1% daily penalties on the delayed €50k.. The maximum amount of penalty for mere delay on the execution period of the contract shall not exceed 10% of the contract value, pursuant to which the Contracting Authority shall have the right to invoke the provisions of Clause 34.2 of the General Conditions. |
| 34.3 | Besides the penalties for delay envisaged in these conditions and without prejudice to all the Contractor’s other liabilities arising out of the contract, should it result to the Contracting Authority that the rate of work of the Contractor is leading to delay in execution, the Contracting Authority may engage other Contractors to carry out the works, or any part thereof at the defaulting Contractor’s expense. The latter shall further be liable to any applicable penalties. |
|  | ### Article 35: Modification to the Contract |
| 35.3 | Further to the provisions of the General Conditions, the CA Supervisor and / or representative and/or AiC shall have the power to order any modification to any part of the works necessary for the proper completion and/or functioning of the works. Such modifications may consist of additions, omissions, substitutions, changes in quality, quantity, form, character, kind, position, dimension, level or line and changes in the specified sequence, method or timing of execution of the works. Such situations would also include instances where changes are imposed or made necessary on the project by third parties / stakeholders following commencement of the works notwithstanding the necessary prior permits being in place and/or any changes resulting from PA permit requirements and/or changes during this process. |
| 35.8 | Subject to what is stated in the Public Procurement Regulations, the Contracting Authority has a right to increase works of a similar nature (repetition of Works) by a maximum of 20% of the contract value which have become necessary to achieve the scope of the contract for the following reasons: - Any minor revisions in the original plans resulting from measurements re-take in the area of works; - Changes in the work methodologies arising from Health and Safety related issues; - Changes required in order to ascertain conformity of the project with the required legislation, regulations, standards, permits, best practices and certificates; - Changes instigated by other competent authorities; |
| 35.9 | Subject to what is stated in the Public Procurement Regulations, the additional works (i.e. new works not included in the original contract) shall be capped at 30% of the contract value for the following reasons: - Any minor revisions in the original plans resulting from measurements re-take in the area of works; - Unforeseen works executed by third party contractors at the same site effecting the works that are being contracted; - Technical advancements which were unforeseen at tender drafting stage; - Changes in the work methodologies arising from Health and Safety related issues; - Changes required in order to ascertain conformity of the project with the required legislation, regulations, standards, permits, best practices and certificates; - Changes instigated by a professional warrant holder who is in charge in the execution of the project or parts thereof, which are felt necessary in order to issue any required professional certifications and, or declarations in order to safeguard associated professional responsibilities and liabilities; - Changes instigated by other competent authorities particularly related to the PA permit; - Additional works that are complimentary in nature to those originally envisaged and required in order to execute the project in its entirety; - Additions which would render the project more economically feasible or cost-optimal; - Changes instigated through developments of the process in functional requirements within the original scope of works as requested by the project beneficiary during the course of works; |
| 35.11 | Should the scope of work be increased or decreased due to factors outside the Contractor's responsibility, no compensation is payable unless the reduction in work exceeds 20% of the initial contract sum. Any claim for compensation will be restricted to the discrepancy between the final certified value and 80% of the original contract price. |
|  | ### Article 39: Quality of Works and Materials |
| 39.1 | Further to the provisions of the General Conditions, works shall be completed in all its parts and finished to its every necessary detail and fitting, notwithstanding any omission or inconsistency in the Specifications and/or Drawings. |
| 39.2 | Further to the provisions of the General Conditions, the Contractor shall be primarily responsible for all quality assurance operations related to all work undertaken under the Contract. Response and turnaround times for tests (including sampling and reporting) by the Contractor shall be within a reasonable range for the specific test but shall invariably be included for verification to the Contracting Authority within the progress report or as otherwise instructed by the CA Supervisor and / or representative. Such results shall be endorsed by both the Quality Assurance Provider and the Contractor’s Perit. The Contractor cannot utilise the services of persons or organisations rendering this service to the Contracting Authority for his/her own testing and certification requirements under the Contract. All testing carried out by the Contractor for quality assurance purpose must be pre-planned and co-ordinated between the Contractor, the QA Provider and the Contracting Authority. The Contractor shall give at least five (5) working days notification to the Contracting Authority before carrying out any testing. Where the QA Provider’s test results and testing procured independently by the Contracting Authority differ, both parties shall deem the Contracting Authority’s results to prevail. |
| 39.4 | The Contracting Authority shall retain the right to seek recourse to further action with the competent accreditation body in case of any reasonable doubts about the reliability of testing results and quality assurance certificates produced for completed works by Contractor. |
| 39.5 | Without prejudice to the provisions of Article 11, following the award of the Contract and during its implementation, the Contractor shall be required to prepare QA reports, endorsed by the QA provider and the Contractor’s Perit (as and when required) for the approval of the CA Supervisor and / or representative (and other Local Authorities). Should the CA Supervisor and/or representative consider any alteration or addition to the submittals and reports mentioned below, as submitted in their last version, the Contractor shall conform therewith without additional costs to the Contracting Authority. The submission to and approval by the CA Supervisor and/or representative of such documents shall not relieve the Contractor of any of his duties or responsibilities under the Contract. The Contractor is bound to provide any revisions to the documents as requested by the Contracting Authority. Where a date is not specified, the Contractor shall provide the requested updated documentation within five (5) working days. The Contracting Authority shall become the owner of these documents, upon submittal by the Contractor, and may be reproduced or used for another purpose, and communicated to third parties, without the consent of the Contractor. |
|  | ### Article 40: Inspection and Testing |
| 40.1 | Further to the provisions of the General Conditions, no work shall be covered up or put out of view without the prior approval of the Contracting Authority. The Contractor shall give adequate time and reasonable advance notice, of not less than forty-eight (48) hours (excluding Saturdays, Sundays and public holidays), The Contractor shall keep photographic evidence showing different stages of works in progress and especially sufficient indicative photographs when encountering buried services. The Contracting Authority may request such evidence at any point during the implementation of the contract. The Contractor shall also be responsible for the performance of any and all testing procedures listed under Section 3 (Technical Specifications) of this document. |
| 40.2 | Further to the Provisions of the General Conditions, the Contractor shall submit test results and certificates to the CA Supervisor and / or representative and include them within all Quality Assurance Reports as described below and as per Table 1 of Article 11.11 of these conditions. The test results shall include the name and address of the Independent Quality Control (QA) Provider performing all the tests, the person responsible of the testing process and the date and location of the tests (by coordinates and referenced on the Proposed layout drawing) being undertaken and other information as the CA Supervisor and / or representative may request. The Contracting Authority may refuse to accept any testing certificates submitted to it if it has reason to believe that results are not being interpreted properly according to Specifications and established codes of practice and methods of testing or that such testing is not fully representative of the Work carried out on site. In such situations the Contracting Authority may carry out its own tests and assessments and shall subsequently abide by its findings. Provided further that the acceptance by the Contracting Authority of positive certificates submitted to it shall not be construed as relieving the Contractor of their responsibilities as guarantor of the Work carried out and of the materials used on the Work. In any case, and without prejudice to the above, the Contracting Authority reserves the right to carry out its own testing of the Work undertaken under the Contract |
|  | Independent QA provider |
|  | - The Contractor shall appoint a QA provider in the form of an independent, accredited testing laboratory to perform all sampling and testing services requiring independent, accredited testing, unless otherwise specified in the specification sections. The testing services shall be both on and offsite as required. - The Contractor shall appoint the QA provider within three (3) weeks from last contract signature date. The Contractor must notify the Contracting Authority of the chosen provider during this same period. The Contracting Authority will then approve or reject the appointment. - A summary report of all field tests containing both “required” and “actual” results plus “passed” or “failed” for conforming, non-conforming, and repeated test results shall be submitted to both the Contractor’s Perit and the CA Supervisor and/or representative with every Interim Payments. |
|  | ### Article 42: Ownership of Plants and Materials |
| 42.2 | Without prejudice to Article 42 of the General Conditions, all temporary works, and materials brought on the site to be incorporated in the works for which payments have been made to the Contractor shall become the property of the Contracting Authority free from any burden, encumbrance and hypothecs. However, Contractor shall be solely responsible for the storage and safety of all materials on site and for the costs incurred in connection to such storage and safety. |
|  | ### Article 43: Payments: General Principles |
| 43.1 | Payments will be made in Euro in monthly interim payments until the final payment against measured works a claim made by the Contractor. This is a Bill of Quantities (BOQ) works contract. Payments shall be authorized by the Contracting Authority and paid by the Treasury Department. It is hereby also being provided, that in affecting interim payments neither the Contracting Authority nor Contracting Authority’s Supervisor nor his/her representative shall be deemed or otherwise construed as having partially or provisionally accepted, in terms of Articles 56 and 57 of the General Conditions, the works for which the interim payments are being made. |
| 43.3 | The period in which payments are to be effected shall be a maximum of sixty (60) days from the date the Contracting Authority receives the invoice. Invoices can only be considered as valid if these are against a measured bill certified by the CA Supervisor and / or representative. |
| 43.6 | Payment shall be made on the following conditions and shall be made as indicated hereunder: - A pre-financing payment of 30% of contract value, against a pre financing guarantee equivalent to the payable amount, in line with Article 44 shall be mandatory. - The Contractor shall receive an interim payment against set milestone equivalent to 15% of the contract value once the Inception Report referred to in Table 1 of Article 11.11 of these Special Conditions have been submitted and approved by the CA Supervisor and/or representative, and mobilisation on site have been carried out. This amount shall be deducted from the first measured bill which shall not be less than 15% of the contract value. - An interim certificate of payment/s may be issued as per Article 48 of these special conditions; - The payment shall be made up to 95% of the value of the works satisfactorily carried out and duly measured, in line with Article 45 of these special conditions; - No claims for compensation arising from failure to understand the conditions of the site/s shall be entertained by the Contracting Authority. |
|  | ### Article 44: Pre-financing |
| 44.1 | Pre-financing under this contract is mandatory. In this case, the prefinancing shall be 30% of the contract amount. The Contractor shall, within fifteen (15) calendar days from the date of last contract signature, furnish the Contracting Authority with a pre financing guarantee equivalent to the payable amount. If the Contractor fails to furnish the pre-financing guarantee required within the prescribed period, the Contracting Authority may consider the contract to be cancelled without prejudice, claim compensation or pursue any other remedy in respect of such failure such as the holding of the performance guarantee and the Contractor will have no claim whatsoever on the Contracting Authority. The pre-financing guarantee shall be in the format given in Section 4 and shall be provided in the form of a bank guarantee. |
| 44.5 | Should the pre-financing guarantee cease to be valid and the Contractor fail to revalidate it, the Contracting Authority may either deduct the amount of the pre-financing from future payments due to the Contractor under the contract or apply the provisions of Article 13.6. |
| 44.7 | Further to Article 44.7 of the General Conditions, the pre-financing payment shall be repaid through percentage deductions in payment certificates as follows: - Deductions shall be made at the amortisation rate of 30% of the cumulative amount of each payment certificate (excluding advance payment and deductions and repayments for retention) in the currency and proportions of the advance payment, until such time as the advance payment has been repaid in full; - The Contracting Authority may at its sole discretion modify as deemed fit the amortisation rate referred to in (i) above for each interim certificate. - The pre-financing guarantee provided for in Article 44 shall be released with the issue of the provisional acceptance certificate. However, the Contractor may request the Contracting Authority to release half of the amount of the pre-financing guarantee when the total amount amortised is equivalent to 50% of the pre-financing payment. |
|  | ### Article 45: Retention Monies |
| 45.1 | A retention of 5% of the value of works carried out shall be retained and will be released in accordance with clause 45.3 of these Special Conditions and the General Conditions. Further to what is being stated in the General Conditions, the Contracting Authority shall retain in total a maximum amount of 5% of the Contract Price and shall be withheld from Monthly Interim Payments and Final Payment. The retention shall commence from the first payment. The retention shall be in the form of a deduction of 5% of the value of works executed and certified for payment under each payment certificate. The Contractor shall submit a retention guarantee. The 100% amount of retained monies will be released thirty (30) calendar days after the submission of a Retention Guarantee. The Contractor shall submit a Retention Guarantee (for which a specimen can be found in Section 4) for the amount of 5% of the value of work executed and certified. |
| 45.3 | The Retention Guarantee (as applicable) shall be released within forty-five (45) calendar days of the date of final acceptance of the works. |
|  | ### Article 46: Price Revision |
| 46.1 | This Contract shall be at fixed prices which shall not be revised. |
|  | ### Article 47: Measurement |
| 47.2 | As stipulated in the preamble of the Bill of Quantities. Any items not covered by the preamble shall be measured in accordance with accepted measurement practice and standards and in compliance with Article 47.1 of the General Conditions. |
|  | ### Article 48: Interim Payments |
| 48.1 | Interim payments may be considered by the Contracting Authority, subject to prior approval by the CA Supervisor and / or representative and/or AiC, based on the following condition, namely only measurable works, which can be tested by the CA Supervisor and / or representative and when documents highlighted in Article 11.11, namely QA & Monthly Progress Reports, of this section are provided by the Contractor. It is hereby being provided also that in affecting interim payments neither the Contracting Authority nor the CA Supervisor and / or representative and / or AiC shall be deemed or otherwise construed as having partially or provisionally accepted, in terms of Articles 56 and 57 of the General Conditions, the works for which the interim payments are being made. |
| 48.2 | Claims for interim payments may be effected for completed and certified works which amount to/exceed €10,000.00 and at intervals of not less than one (1) month. |
|  | ### Article 49: Final Statement of Account |
| 49.1 | The draft final bill, and further proceedings related thereto, shall be dealt with before the issuance of the provisional acceptance certificate. The Contractor shall submit to the CA Supervisor and / or representative a draft final bill with supporting documents showing in detail the value of the work done in accordance with the Contract, together with all further sums which the Contractor considers to be due to him under the Contract in order to enable the CA Supervisor and / or representative to prepare the final bill. |
|  | ### Article 56: Partial Acceptance |
| 56.1 | Further to the Provisions of the General Conditions, upon practical completion of works, the Contracting Authority may issue a partial provisional acceptance certificate. |
|  | ### Article 57: Provisional Acceptance |
| 57.1 | Further to the provisions of the General Conditions, works shall be considered taken over when: - All the work in the contract has been completed and certified, including snags. - Final Report as described below and as per Table 1 of Article 11.11 of these conditions, is submitted and approved by the CA supervisor and/or representative; |
|  | Final Report |
|  | - Upon completion of the works, the Contractor shall provide the CA Supervisor and/or representative with a final report which shall include the following: - Final QA Report - As Built Drawings - Photographic Survey - Final H&S Report - O&M Manuals (where applicable) - Applicable MCCAA certifications - Applicable Planning Authority Compliance Certificates - Warranties and Guarantees - Preventive and Reactive Maintenance Plan - The Final Report shall be prepared to the satisfaction and approved by the CA Supervisor and/or representative. |
|  | ### Article 59: Final Acceptance |
| 59.1 | Further to the provisions of the General Conditions, upon expiry of the defects liability / retention period, the Supervisor shall issue the Contractor a final acceptance certificate. Retention monies and guarantees shall be paid/released within 60 days from the issue of the Final Acceptance Certificate. |
|  | ### Article 66: Dispute Settlement by Litigation |
| 66.1 | If no settlement is reached within one-hundred and twenty (120) calendar days of the start of the amicable dispute-settlement procedure, each Party may seek: - either a ruling from a Maltese court, or - an arbitration ruling, in the case where the parties, i.e. the Contracting Authority and the Contractor, by agreement decide to refer the matter to arbitration. |
|  | ### Article 68: Administrative and Financial Penalties |
| 68.2 | Without prejudice to the provisions of application of penalties as laid down in the Contract, these shall be applicable as listed below: Clause; Applicable Penalty. SC 11.8; Penalty of 0.1% of the Contract value per calendar day of mere delay for each calendar day following the deadline for failing to execute an administrative order.. SC 15.5; Penalty of two hundred euro (€200) for each calendar day following the set deadline for failing to submit detailed Programme of Works as requested in the provisions of Clause 15.3.. SC 20.11; Penalty of five hundred euro (€500) for every site visit report with infringements which have not been addressed within the specified deadline.. SC 34.1; Penalty for every day’s delay in performance from the approved Programme of Works for the contract. The applicable daily rate as well as the maximum amount shall be as per formula provided in Article 34.1.. The maximum amount of total damages shall not exceed 20% of the contract value, pursuant to which the Contracting Authority will have the right to invoke the clauses related to the termination of the contract and subsequent penalties. The Contracting Authority reserves the right to withhold penalties from future payments to the Contractor or to deduct them from the performance guarantee or retention monies. |
|  | ### Article 71: Summary of Contract Timelines |
| 71.1 | Without prejudice to the provisions of the General and Special Conditions, the following is a summary of contractual timelines that Contractual Parties needs to abide with: Activity; Responsible Contractual Party; No of Days to provide document; From. Contract Signature; Contractor; 15 Calendar Days; Receipt of Contract Agreement. Performance Guarantee forwarded to the Contracting Authority; Contractor; 15 Calendar Days; Receipt of Contract Agreement. Prefinancing Guarantee forwarded to the Contracting Authority; Contractor; 15 Calendar Days; Date of last signature on contract. Take out all insurances provided for in Article 14 of these Conditions; Contractor; 3 Calendar Weeks; Date of last signature on contract. Inception Report; Contractor; 3 Calendar Weeks; Date of last signature on contract. Appointment of QA provider; Contractor; 3 Calendar Weeks; Date of last signature on contract. Order to Start Works (OTSW); Contracting Authority; 8 Calendar Weeks; Date of last signature on contract. Commencement Date; Contracting Authority; Date stipulated in the OTSW; NA. Final Report; Contractor; NA; Prior to the date of Provisional Acceptance. Release of retention guarantee; Contracting Authority; 45 Calendar Days; Date of Final Acceptance. Drawings; Contractor; 15 calendar days; Request by CA Supervisor and/or representative. Testing; Contractor; 5 calendar days; Notification to CA Supervisor and/or representative. Change of Key Expert Notification; Contractor; 10 calendar days; Before change of Key Expert. |

SECTION 4 –SPECIFICATIONS (Note 3)

Note: Where in this tender document a standard is quoted, it is to be understood that the Contracting Authority will accept equivalent or better standards. However, it will be the responsibility of the respective bidders to prove that the standards they quoted are equivalent or better to the standards requested by the Contracting Authority.

|  | ### PREAMBLES |  |
| --- | --- | --- |
|  | Preamble to the Technical Requirements |  |
|  | - These specifications outline both the general and specific requirements for the project, delineating the expected quality of materials and the standard of workmanship to be employed. - All costs related to the Preambles, stated or implied, direct or indirect are deemed to be included within the other quoted rates for the works within the bill of quantities. - The description primarily focuses on the principal materials, construction, and restoration operations typically involved in such endeavours. Should the Scope of Works necessitate additional details, the Contracting Authority will issue supplementary information before amending the relevant tasks. - It is essential to read these specifications alongside the other documents encompassed in the Technical Requirements, including the Drawings, Special Conditions, as well as the Bills of Quantity. - The Contractor bears full and sole responsibility for adhering to and applying the standards, laws, and regulations governing the Works covered by this contract. Consequently, all contract rates are presumed to encompass the assumption of these responsibilities and the fulfilment of associated obligations. - The Contractor shall be responsible for: - Provision of any statutory works permits/licenses and other necessary authorizations to carry out the Work assigned; - Provision of temporary measures such as mobile toilets and first aid measures, for the welfare of the contractor’s employees on site. - Implementation and upkeep of appropriate traffic management plans, and health and safety management; - All necessary construction works including mechanical/electrical works, and internal finishes, as well as commissioning of the Work in accordance with approved plans, permits and contract commitments as applicable to the Work; - Any remedial measures to the completed Work to ensure its satisfactory performance after completion. - The Contractor shall comply with and fulfil all obligations imposed by Article 19 of the Police Laws and shall give all notices, obtain all permits; pay all fees that may be lawfully demanded by Public Officers in respect of works and comply with all requirements of the Law and any Lawful Authority. - In general, all materials to be integrated into the Works must represent the highest quality within their respective categories, devoid of any damage, flaws, or defects that could jeopardize their integrity, appearance, performance, or durability. - The Contractor is obligated to take all necessary measures to adhere to Construction Site Regulations, Health and Safety Requirements, and any other statutory obligations related to Construction/Building Works stipulated by the Laws of Malta. - In addition to conforming to the specifications provided, both the Contractor and its Perit must ensure that the Works are executed in complete accordance with the terms and conditions of the relevant Planning Permission issued by the PA. This includes compliance with all approved documents, such as Drawings and the Method Statement associated with the project. - Any works, materials, or portions thereof identified by the CA Supervisor and/or representative as not conforming to the requirements outlined in the bidding Documents must be replaced at the expense of the Contractor. - Despite the subdivision of these Specifications into different sections, each part is considered supplementary and complementary to every other part. Unless explicitly stated otherwise, the cost of compliance with these specifications is presumed to be included in the Contract Price. - Wherever in this Section – Technical Specifications the Contractor is required to submit a document, report, literature, information, drawings, method statements, calculations, designs, information, samples etc., it is to be understood that the time limit for the submission/s shall be strictly as indicated herein. In those instances where this time limit is not indicated, it shall be invariably understood as being of fourteen (14) calendar days. |  |
|  | Architect in Charge |  |
|  | - The Architect in Charge shall be appointed by the Contracting Authority. - The Architect in Charge reserves the right to reject any part of the Works, which is not executed to the best practice and/or not compliant with the technical specifications/drawings. All rejected work shall be demolished and rebuilt and/or reinstated in new materials at the Contractor's expense, without any extension of the Contract time. - The contractor shall provide drawings for all design & build works, to be approved by the Architect in Charge. - The Architect in Charge reserves the right to request any drawings/method statements/reports he/she may deem important for the attainment of the required aesthetical, structural and functional results. - All Items, works and/or products which are part of this tender, and including items which are not necessarily detailed in the technical specifications, shall be subject to approved technical literature, samples, mock-up areas and/or methodology, as may be requested by the Architect in Charge. |  |
|  | Regulations |  |
|  | - The execution of works and operations will be governed by the following regulations, including but not limited to: - Chapter 646 of the Laws of Malta (Occupational Health and Safety Authority Act), - SL 646.03 - Work Places (Health, Safety and Welfare) - SL 646.11 - General Provisions for Health and Safety at Work Places Regulations. - LN 5/2006 - Control of Legionella Regulations - LN 136 of 2019 & LN 468 of 2021 - Avoidance Of Damage To Third Party Property Regulations, - LN 281/2004 - Work Place (Minimum Health and Safety Requirements for Work at Construction Sites) Regulations, - LN 295/2007 - Environmental Management Construction Site Regulations, - SL 623.08 - Construction Management Site Regulations - SL 623.09 - Construction Industry Licensing Regulations - SL 623.11 - Construction Site Insurance Obligations Regulations - Any specific requirements periodically specified by the responsible authorities must be followed. - The contractor shall abide to new, updated and concurrent national or EU regulations, legislations, standards, and/or code of practice which are and/or become applicable during contract implementation. These shall be applied in consideration of the Contractor's specific operational context and the nature of the work activities. |  |
|  | European Standards and Codes of Practice |  |
|  | - Where applicable, Malta Standards Authority Standards (MSA-EN Standards), European Standards (Harmonised EN- Standards, or European Technical Approvals), or International Standards (ISO- Standards), in this order of priority, shall be used to determine satisfactory performance. - Throughout this document, the specification, and drawings, efforts have been made to reference the applicable European Standards whenever possible. In cases where a pertinent European Standard was not accessible during the document's preparation, reference has been made to British Standards or other relevant standards. It is important to note that all standards cited in this document will be overridden by the most recent standards published. - In instances of conflict or ambiguity, the relevant EN, BS, or other Code of Practice will be chosen and communicated to the Contractor by the CA Supervisor and/or representative. The decision of the CA Supervisor and / or representative in this regard will be considered final. - It is the responsibility of the Contractor and their Perit to abide by the latest and applicable standard, regulations, guidelines and/or codes of practice. |  |
|  | Certification |  |
|  | - All works, systems or equipment which need to be certified by law or by any legal notice, are to be so certified by a person/body as contemplated by the same law/legal notice. Such certifications shall be forwarded to the Contracting Authority with all the other contract drawings and information. - In any case, all systems installed shall be certified by the Contractor’s Experts for design, installation, testing and commissioning - Any related costs shall be included in the tender rates. |  |
|  | General Site Management & Other Requirements |  |
|  | Site Extents and Limitations of Use |  |
|  | - The Contractor is responsible for implementing all necessary protective measures to prevent damage to other existing structures as well as services and facilities within and adjacent to the site. Strict adherence to instructions or guidelines from all the relevant authorities, and monitors engaged to supervise the works, is mandatory. To facilitate this, the Contractor must have a permanent on-site representative authorized to receive and act upon instructions. |  |
|  | Site Constraints |  |
|  | - The Contractor is required to verify that the existing levels and site conditions correspond to the information provided in the drawings. Any discrepancies identified by the Contractor should be promptly communicated to the CA Supervisor and/or representative for resolution. - Having visited the site, the Contractor is presumed to be fully acquainted with the site conditions, associated risks, access restrictions, and work constraints. - Throughout all stages of the work, the Contractor must ensure that external areas and access roads are left in a clean and orderly condition. Heavy construction vehicles are to follow specific routes to and around the site. - The Contractor is responsible for coordinating works with any other Contractors simultaneously operating within or adjacent to the site. - The Contractor must account for the impact of the mentioned constraints and similar factors on their activities to ensure the timely completion of the works. Consequently, no claims related to these matters will be entertained. - The contractor shall take all necessary measures and precautions in order to avoid any disruptions to the operations of Dar il-Kaptan. |  |
|  | Building File |  |
|  | - The Contractor is required to maintain the Building File onsite, encompassing all documentation accumulated throughout the project's duration. - The Building File should incorporate design information, details about the materials and elements delivered to the Site, and information introduced during the construction phase, including "as-built" details, proposed program specifics, certificates for operating plant and equipment, and information concerning significant hazards or work sequences. - The Building File shall be available for review throughout the course of the works and submitted to the CA Supervisor and/or representative at the end of the Works. |  |
|  | Workmanship |  |
|  | - The craftsmanship of all elements must adhere to the standards outlined in BS 8000, "Workmanship on Building Sites." When applicable, standards set by the Malta Standards Authority (MSA-EN Standards), European Standards (Harmonized EN-Standards or European Technical Approvals), or International Standards (ISO Standards) will be utilized in order of priority to ascertain satisfactory performance, unless otherwise specified in the Specification. - Tolerances in building shall comply with the relevant section of BS 6954. - Throughout the course of these works, precautions should be taken to minimize vibrations, preventing any disturbance to the existing structure and surrounding areas. - Preservation measures must be implemented to safeguard topsoil and original horizontal surfaces from contamination with subsoil, debris, stones, or hardcore, as well as protection against exposure to harmful substances like petrol, oil, lime, or cement. - It is the Contractor's responsibility to ensure that all chemical agents used do not leave harmful by-products, such as soluble salts, avoid leaving a more uneven surface, and are applied according to the manufacturer's recommended guidelines. |  |
|  | Material and Components |  |
|  | - The contractor shall give all necessary notices to authorities concerned and shall allow them facilities for removing any fixtures, fittings, or services, which may belong to them. - All materials resulting from gutting out, cleaning, demolition, and restoration activities must be transported away from the site using rubber-tyred wheelbarrows and/or rubber-tyred shovels/bob-cats. They should be conveyed to an approved dumping site, and all associated fees and expenses, as applicable, are to be included in the rates for the works. - In general, all materials shall be free from Volatile Organic Compound (VOC) unless stated otherwise. |  |
|  | Waste |  |
|  | - Construction waste shall not be allowed to accumulate on site and should be removed periodically (timing to be agreed with the CA Representative). The contractor shall endeavor to locate the storage and stockpile areas in the areas from where there will not be a significant visual impact on views of the fortifications. Waste is to be separated in different skips as per Environmental (ERA) Regulations and as approved by the CA Representative. - No rubbish (skips) is to be left unprotected/uncovered overnight, especially combustible, and inflammable rubbish. Skips are to be or closed/covered skips or enclosed within a protected area. Amount of rubbish not to exceed tip of skip level. - All activities producing dust shall be controlled, and measures such as spraying with water shall be used to ensure that the emitted dust is minimised. Dust-laden materials shall be removed from the site, and transported through public thoroughfares, only after thorough watering before leaving the site. Dust covers, of appropriate material, properly secured along all sides, shall be used on all open-topped vehicles used for the transportation of rubbish or debris from the site. |  |
|  | Control of Noise and Vibration |  |
|  | - All plant and site operations will be required to conform to the relevant laws and regulations, permits and applicable standards in relation to the control of noise and vibrations. |  |
|  | Defective work and materials |  |
|  | - All rejected work shall be removed and replaced using new materials at the Contractor’s expense. - The Contractor shall also be bound to replace any defective materials in all or parts of the existing Works by proper materials and/or workmanship as directed by the CA Supervisor and/or representative. - The Contractor is liable for the replacement works and interventions as requested by the CA Supervisor and/or representative. |  |
|  | Completion |  |
|  | - Prior to the issue of any Provisional Acceptance certificate, the Contractor shall clear away and remove from that part of the site to which such Provisional Acceptance certificate relates, all Contractors’ Equipment, surplus material, rubbish and Temporary Works of every kind, and leave such part of the Site and Works clean and in a workmanlike condition to the satisfaction of the CA Supervisor and/or representative. - Provided that the Contractor, shall be entitled to retain on Site, until the Defects’ Liability Period, such materials, Contractor’s Equipment and Temporary Works as required by him for the purpose of fulfilling his obligations during the Defect’s Liability Period. |  |
|  | Health and Safety |  |
|  | General |  |
|  | - The Contractor must ensure that: - all activities will adhere to Health & Safety regulations and any other relevant regulations and Codes of Practice. - all activities will conform to the approved Health & Safety Plan, which will be adjusted as necessary based on evolving site conditions and constraints. - site specific risk assessment will be undertaken and if significant hazards are identified a specific risk assessment will be undertaken and recorded. - control measures will be implemented as required in response to specific hazards. - The OHSO shall carry out continuous risk assessments and be answerable to both Contracting Authority, and the Contractor. - He shall be responsible for coordinating with the Health and Safety Supervisor appointed by the Contracting Authority in accordance with the Occupational Health and Safety Authority Act, (Chap. 646 of the Laws of Malta). - He shall also be responsible for notifying all relevant authorities of any accidents, and for reporting to the Contractor and the Contracting Authority on all such incidents. |  |
|  | First Aid Facilities |  |
|  | - The Contractor shall provide first aid facilities on the site equipped with first aid kits, and relevant medical supplies, and shall be required to respect designated emergency access routes defined in the Health and Safety plan. |  |
|  | Temporary Electrical & Water Supply |  |
|  | Temporary Electrical Installation (where applicable) |  |
|  | - The Contractor shall provide temporary electrical installation onsite. - Any temporary electrical installation on the Site shall meet the requirements of the IEE Regulations for Electrical Installations, EneMalta Regulations and any relevant standards. Any temporary electrical installation shall be certified by a licensed electrician and/or the Electrical Engineer, every 6 months, and the certificate shall be affixed in a prominent position next to the Main Temporary Switchboard. - Failure to comply, or to update this certificate, will lead to an automatic penalty of €250 per day. - Any costs related to the provision and consumption of temporary electrical supply are deemed as already included in the contract rates. - The contractor shall take all necessary procedures to control energy use on site. Site lighting shall be, as much as possible, low energy, or energy-efficient, light fixtures |  |
|  | Temporary Water Supply (where applicable) |  |
|  | - The Contractor shall provide temporary water supply for the execution of works. Any costs related to the provision and consumption of temporary water supply are deemed as already included in the contract rates. |  |
|  | Billboard and Notification Board |  |
|  | Environmental Management Construction Notice Board |  |
|  | - The Contractor shall also be responsible for the provision of three (3) notification boards measuring 2.5m by 1.5m as per relevant Legal Notice. The notification boards shall be of a material suitable to resist the effects of the weather for the duration of the works, and shall be securely fixed in locations as instructed by the CA Supervisor and/or representative. |  |
|  | Publicity Billboard |  |
|  | - The Contractor is also tasked with the provision, erection and upkeeping a Project Information Board Billboard, measuring 5.0m by 3.0m (+/- 10%). A sample of the artwork, including its dimensions and the board's location, will be specified, and mutually agreed upon onsite. Upon Contract award, the Contracting Authority will furnish the final artwork for the board, which will be supplied to the Contractor. The design of the board must be submitted for approval by the Contracting Authority. - In the case of any irreparable damage to any 'project Board' billboards, the contractor shall bear full responsibility for their replacement. |  |
|  | Bill of Quantities |  |
|  | General |  |
|  | - The bill of quantities must be read with all the other contract documents and the Contractor shall be deemed to have thoroughly acquainted himself with the detailed descriptions of the works to be done and the way in which they are to be carried out. All the works must be executed to the satisfaction of the CA Supervisor and/or representative. - The items in the bill of quantities, the quantities listed, and the prices apply to the whole of the Works carried out under this Contract. - Post-contract re-measurement shall be in accordance with the Preambles stated in this clause. - The quantities set forth against the items in the bill of quantities are an estimate of the quantity of each kind of the work likely to be carried out under the contract and are given to provide a common basis for bids. There is no guarantee to the Contractor that he will be required to carry out the quantities of work indicated under any one particular item in the bill of quantities or that the quantities will not differ in magnitude from those stated. Furthermore, there is no guarantee to the Contractor that the overall value of the works will not differ in magnitude. - When pricing items, reference should be made to the conditions of contract, the technical specifications and related annexes, and relevant drawings for directions and descriptions of work and materials involved. - Save where the technical specifications or the bill of quantities specifically and expressly state otherwise, only permanent works are to be measured. Works will be measured NET to the dimensions shown on the drawings, or as updated by the Contractor’s Perit or ordered in writing by the CA Supervisor and/or representative, save where described or prescribed elsewhere in the contract. - Measurements for Design and Build elements shall be made in line with Article 47.1(a) of the General Conditions. - In adjusting extras or variations on the contract, works will be measured on the same basis as that on which the quantities were prepared. All works not specifically mentioned in the bill of quantities will be taken as included in the prices of various items. - No allowance will be made for laps and loss of materials or volume thereof during transport, placing and/or compaction or for any wastage. - All works shall be measured net as laid. Rates are to include for all waste and straight or raked cutting. - Material, colour and finish shall be strictly compliant to the specifications and / or as agreed with the CA Supervisor and/or representative. - Unless otherwise specified elsewhere in the procurement documentation, the Contractor shall submit standard RAL colour or approved equivalent, for the finishes, furniture and equipment, for selection and approval of colour by the Contracting Authority. |  |
|  | Units of Measurement |  |
|  | The following units of measurement and abbreviations shall be used: |  |
|  | Millimetre | mm |
|  | Metre | m |
|  | Square metre | m2 |
|  | Hectare | Ha |
|  | Cubic metre | m3 |
|  | Kilogramme | Kg |
|  | Tonne (1000 kg) | t |
|  | Sum | Item |
|  | Number | No. |
|  | Hour | Hr |
|  | Kilometre | Km |
|  | Per cent | % |
|  | Man-day | m/d |
|  | Calendar week | Week |
|  | Working Day | Day |
|  | Hours | Hr |
|  | Provisional Sum | Prov Sum |
|  | Terms relating to payments |  |
|  | - The method for measuring completed works for payment must be in accordance with the Contract. - Any provisional sums (where applicable) in the bill of quantities must be used at the discretion of the Contracting Authority or as otherwise set out in the contract. |  |
|  | Pricing |  |
|  | - The prices and rates inserted in the bills of quantities are to be the full inclusive values of the works described under the items including all necessary and ancillary works, supplies and services deemed necessary for the proper completion of the works, including and not limited to the following: - Provision for working both by hand and machinery, including all double and multiple handling as deemed necessary. - Compliance with statutory obligations and the regulations of any Authority, Public Service or Statutory Undertaker relating to the execution of the Works. - Labour and all costs in connection herewith including transporting to and from site and any hoisting required. - Comply with all requirements stated or implied under Section 2 of the Technical Specifications - Key Experts, Other Experts and Subcontractors. - Costs related to site visits and progress meetings by Contractor’s Key Experts and/or other experts, as required by CA Supervisor and/or representative. - Provision of making all the necessary consultation and arrangements with other stakeholders that are involved in the works. - Insurances listed in Article 14 of the Special Conditions. - All plant, vehicles, tools, machinery and equipment (both those referred to in the procurement documents, and those which were not) required to execute the works in accordance with the specified standards and inclusive of any applicable certifications. - Any technical literature, O&M manuals and tests certificates requested by the CA Supervisor and/or representative and those required to comply with the provisions of the contract. - Any documents stated or implied by the contract including but not limited to shop drawings, as-built drawings, construction/ working/ fabrication drawings, digital photographic records, manufacturer’s documents, reports, payment application, and other documents. - Supply and delivery to site of materials, equipment and goods, storage, shifting and double/multiple handling as necessary and all costs in connection herewith. - Allowance for working outside normal working hours (Example working during the night, Weekends and Public holidays etc) to limit inconvenience to the public, to enable use of equipment not normally permitted during normal working hours, etc). - Removal from site of all waste materials and debris to an authorized dumping site and inclusive of all dumping charges. - Cleaning of the roads, Contracting Authority’s and third party properties, etc from dust and/ or other materials generated by the works and for maintaining a dust-free environment - Provision of all necessary shoring, propping, supports, screens required for all the works, and for protection of all third party property as deemed necessary. - Provision of all works around recesses and projections. - Fixing, erecting and installing or placing of materials, equipment and goods in position. - Surveying services wherever levels, setting out, alignments and other are required prior to commencement of works. - The Contractor shall be responsible for taking detailed measurements on site. The price quoted by the Contractor shall include for all those materials, components, assemblies, fixtures, equipment, plant, or tests that are required to achieve the design intent illustrated in the drawing plans, as well as the performance specifications included in this document. - For walls; all mortar needed, labour required for returns, edges, angles and part courses centering, all formation construction and finishing of joints between walls and concrete elements, fixtures, fittings, branches and ancillary adhesives required to install drainpipes in wall cavities. - For concrete: provision of concrete to the required specifications to all levels and heights, any additional admixture, plant or labour arising from the nature of the works or the contractor’s methodology; associated plant required in connection with the placing of concrete, such as transport, craneage, scaffolding, staging, pumping, vibration, etc; all necessary formwork, at any height, to achieve the required finish, in accordance with the technical specifications, annexes and drawings; all vibration, compacting, curing and protection of cast-in-situ and pre-cast concrete elements; all testing required during the course of works; all necessary checks for levels, plumbness and alignment. - For steel reinforcement; lapping and bends. - For painting works; price quoted by contractor is deemed to include the achievement of a satisfactory painted surface finish as approved by the CA Supervisor and/or representative. NO extra payments for extra coats of paint will be made for unsatisfactory painted surfaces. - For Plastering works: Rates are deemed to be inclusive of preparatory and making good (sbuzzar) for plastering works in any type of voids, gaps, openings which are present in walls and ceilings after construction phase. No extra claims will be entertained for such items. - The effect of phasing the works as set out in the Contract documents, local conditions and restrictions by the Local Authorities, Terminal Operators and Port Operations that are likely to affect the execution of the Works. - All temporary works (including any shuttering) and installations, other than those itemised. - All general obligations, liabilities and risks involved in the execution of the works set forth or reasonably implied in the Contract documents. - Allow for scaffolding, high-up, lifter and/or cranage as and where necessary to carry out the works indicated in this bill unless specified elsewhere in the bill. The scaffolding system to work in full compliance with the provisions of the Health and Safety Act. - Establishment charges, overheads, profit and allowances for all obligations. - Inclusive and compliant to the local OHSA Regulations. - The tenderer is deemed to have visited site prior to pricing and submitting his tender. No claims which result from the tenderers failure to visit the site will be accepted during or after the execution of the works. - Where the contractor’s note a discrepancy between the drawings supplied to the contractor and the works required on site, he shall bring this to the attention of the CA Supervisor and/or representative and shall require approval form the CA before commencement of works. - Where the contractor cannot perform the works with a methodology indicated in the se procurement documents, the CA Supervisor and/or representative shall provide a way forward before the commencement of work. |  |
|  | Mobilisation and demobilisation |  |
|  | - Mobilisation and demobilisation of all plant and equipment, unless otherwise stated separately, is deemed to be included and also deemed to include for all costs throughout the contract including where multiple mobilisation and demobilisation is necessary as work progresses and/or due to weather conditions and/or site restrictions and operations. |  |
|  | Taxes |  |
|  | - All prices, Lump Sums, and rates entered in the Bills of Quantities are to be exclusive of VAT but including all taxes, duties and any charges as applicable. |  |
|  | Completing the Bill of Quantities |  |
|  | - In the bill of quantities, rates and prices will be entered in the appropriate columns in Euros - Errors will be corrected as follows: - where there is a discrepancy between amounts in figures and in words, the amount in words will prevail; and - where there is a discrepancy between the unit rate and the total amount derived from the multiplication of the unit price and the quantity, the unit rate as quoted will prevail. |  |
|  | Day rates (where applicable) |  |
|  | - Rates shall include for all preliminary items as detailed in these preambles, including but not limited to: - Labour: transport costs, staff bonuses, holidays, taxes, insurances, subsistence or lodging allowances and periodic travel allowances, small tools, Head Office charges and profit, etc. - Plant and equipment: mobilisation and demobilisation costs, drivers and operators unless otherwise stated, fuel and consumables, repairs and maintenance, insurances, Head Office charges and Profit, etc. - Materials and Equipment: delivery to works’ site including loading and unloading, storage and multiple handling of same, any wastage, Head Office charges and Profit. |  |

|  | ### EXPERTS REQUESTED |  |  |
| --- | --- | --- | --- |
|  | Key Experts |  |  |
|  | - The Contractor/s shall have at his/her disposal the services of the following Key experts, who must be in possession of the minimum criteria listed below. Key Expert No.; Description; Qualifications & Experience. 1.; Contractor’s Perit; - In possession of a Warrant to practice as a Perit in Malta issued by the Warranting Board as per Periti Act Chapter 390 OR Shall hold an approval of Temporary Service by the “Board tal-Warrant Tal-Periti” of Malta for the provision of civil engineering services in Malta. Proof of compliance to this requirement is to be provided OR If the approval of Temporary Service by the “Board tal-Warrant Tal-Periti” is still in process, the correspondence for application with the “Board tal-Warrant tal-Periti” must be submitted as part of the tender bid. In this regard the approval of Temporary Service by the “Board tal-Warrant Tal-Periti” must be in place before the signing of the contract. - Shall be fluent in Maltese and/or English.. 2.; Site Manager (Full-time); - Have a minimum qualification of MQF Level 4 (or equivalent). - Shall be fluent in Maltese and/or English.. - Key experts shall attend any meetings and be on-site during the course of the works as and when requested by the Contracting Authority. Otherwise fines as per Special Conditions will apply. - N.B.: the same person cannot be nominated to cover more than one of the below roles. - It should be highlighted that the Contracting Authority shall ONLY entertain requests by the Contractor to substitute Key Experts, if proposed substitute fulfils completely the requirements as set out in this Contract. - It is the responsibility of the Contractor to also comply with all the requirements of Legal Notices 295 of 2007 and 136 of 2019 regarding the engagement of applicable experts. |
|  | Key Expert 1 - Contractor’s Perit |  |  |
|  | The role of the Contractor’s Perit includes but not limited to the following; - Shall act as the Team Leader of the Key Experts and Other Key Experts and be responsible to liaise with the different Key Experts under this Contract for the successful completion of the works. - Shall be responsible for the project management i.e. running of the Contract obo the Works Contractor to ensure the timely delivery of the works within the budget and quality requested. - Be the Contractor’s representative and the main point of contact of the works under this Contract and shall be the main liaison of the Works with the CA representative and / or AiC on behalf of the Contractor. - S/he shall liaise between the different Contractors onsite including Third Party Contractors. - Shall be responsible to manage the sub-Contractors. - Shall supervise the works and certify that they are according to Contract requirements, permits, standards, laws and regulations. - To set-up, approve and implement the Quality Assurance (QA) and Control Plan (CQP). - As part of the Quality Assurance, shall issue a signed declaration containing and confirming the following; - The works carried out are structurally stable. - The steel reinforcement provided conforms with the approved construction drawings. - Quality Assurance certificates are published by an independent accredited testing laboratory for concrete works. - Membrane and waterproofing works’ certificates and welding certificates. - Leak-proof testing Certificates for water retaining structures - All works under the Contract were conducted and provided according to all applicable regulations, standards and Contract requirements. - The works have been performed in accordance to the manufacturer’s instructions (when applicable). - Other declarations as necessary and as required by the Contracting Authority. - Attend all the necessary technical and progress meetings as requested by the Contracting Authority and as necessary. - Carry site visits as necessary to ensure compliancy of the works. - Check and sign land surveys prior to submission to the Contracting Authority. - Prepare and submit as-built signed drawings for all the works including but not limited to the construction works, building services and finishes to the Contracting Authority. - Check and sign the measured bill of quantities prior to submission to the Contracting Authority. Responsible for measurements, compute valuation of works, endorse claims etc. - Prepare and submit construction/working/shop drawings as necessary for works progress or as directed by the Contracting Authority. - Prepare and submit detailed drawings of specific works in cases where revisions from the contract drawings are required. - Identify and adopt the particular/relevant specifications in the works as necessary. - Be responsible for communicating any technical issues with the Contracting Authority in a timely manner and shall in liaison with the Contractor and Project Manager seek to resolve same. - Produce drawings during the implementation process whenever requested by the Contracting Authority. - Must take charge of project progress and ensure that it is completed on time. - S/he shall attend meetings as requested by the Contracting Authority and take Minutes of Meetings whenever requested. - Must prepare a detailed Programme of Work and keep it updated as requested by the Contracting Authority. - Must closely work with the OHSO Key Expert and CA Project Supervisor (H&S) and ensure that any remedial measures are being implemented and that the Health & Safety Plan is being adhered to. - Must apply cost control and any variations/modifications are to be immediately communicated to the Contracting Authority for approval prior to execution. - S/he shall be available during the duration of the whole works and be available 24/7 in case of emergencies. - Must ensure that all the Contract’s Obligations are being met. - S/he shall be available during the duration of the maintenance period of the Contract. - Responsible to maintain the building file on-site. It should include drawings and design, details about the materials and elements delivered to the Site, and information introduced during the construction phase, including "as-built" details, certificates for operating plant and equipment, and information concerning significant hazards or work sequences. |  |  |
|  | Key Expert 2 - Site Manager (Full-Time Basis) |  |  |
|  | The Contractor shall employ a Site Manager based full-time on site. The role of the Site Manager shall be the overall management and control of the work, including work carried out by any Subcontractors. The following are the minimum responsibilities: - Responsible as a site manager in terms of Chapter 623 of the Laws of Malta for the management of a construction site, ensuring that any permits, certifications, authorisations, or any such clearances required for any portion of the construction works are in place. - Responsible for the forbidding of access to site and for reducing pollution related to noise and dust emissions. - Organization, co-ordination, supervision and control of all work, including Subcontractor’s work. - Be responsible for all necessary Building Construction Authority (BCA) documentation, including but not limited to, commencement notice, site management responsibility form, and if applicable, compile condition reports and method statements (in accordance with the BCA regulations) for the proposed development which may include demolition, excavation and building works. Liaison with the CA supervisor and/or representative to ensure technical conformity of the works. - Management of foremen and leading hands. - Ensure adherence to Work Methods, and Health and Safety, Security and Environmental plans, risk mitigation measures, procedures and instructions. Cooperates with the Contractor’s OHSO and the CA Supervisor and/or representative as necessary and to rectify and prevent non-conformities. - Ensure that works are carried out according to the Contractor’s Quality Plan. |  |  |
|  | Other Experts |  |  |
|  | - Other Experts are other professionals required on an ‘if and when required basis’ which are necessary for the full completion and certifications of the works. The Contractor shall engage other experts as deemed necessary, with any related costs borne by the contractor. Bidders are not requested to submit details of the Other experts listed below at tendering stage but may be requested to submit details within ten (10) working days from the request made by the CA Supervisor and/or representative. - These other experts shall include: |  |  |
|  | Description of Role |  | Qualifications & Experience |
|  | Site Technical Officer (STO) The role of the STO includes but not limited to the following; - The STO shall ensure enforcement of the method statement approved covering the specific works to be executed. - The STO needs to be present on-site and fulfil his/her duties according to L.N.136 of 2019. |  | - In possession of Warrant to practice as a ‘Perit’ or ‘Inginier’ and - registered with the Building and Construction Authority to act as an STO. |
|  | Warranted Electrical Engineer The role includes but not limited to the following; - Supervision of the electrical installation - Responsible for the electrical installation - Approve and endorse drawings (proposed & as-fitted) - To submit the certificates requested during and after works completion related to the electrical installation. Responsible for the installation of the electrical system and supply. - Certify all test results and confirm that the installation is in accordance with the Regulations. - To sign the certifications for the application of the single phase or three phase application and/or shifting of meters - Provision of services during maintenance period. - Co-ordinate with the Utilities Services Operators as required. |  | - Be in possession of a valid warrant issued and acknowledge by the Engineering Board in Malta, enabling the individual to practice his/her profession in Malta. |
|  | Warranted Mechanical Engineer The role includes but not limited to the following; - Responsible for the mechanical installation. - To submit the certificates requested during and after works completion. - Certify mechanical systems (incl. HVAC, plumbing, lifts, fire protection system) as compliant with any relevant regulations, standards, and Contract requirements. - Issue and endorse drawings and reports. - Assist in preparing applications for the provision of water services on site. - Provision of services during maintenance period. - Co-ordinate with the Utilities Services Operators as required. |  | - Be in possession of a valid warrant issued and acknowledge by the Engineering Board in Malta, enabling the individual to practice his/her profession in Malta. |
|  | Licensed Mason The role includes but not limited to the following; - To act as the mason according to the commencement notice to be submitted to the Contracting Authority. |  | - Must have a valid mason license and be registered with the Building and Construction Authority. |
|  | Wireman The role includes but not limited to the following; - Supervision of the electrical installation - Responsible for the electrical installation - Approve and endorse drawings (proposed & as-fitted) - To submit the certificates requested during and after works completion related to the electrical installation. Responsible for the installation of the electrical system and supply. - Certify all test results and confirm that the installation is in accordance with the Regulations. - To sign the certifications for the application of the single phase or three phase application and/or shifting of meters - Provision of services during maintenance period. |  | - Shall possess a valid wireman license B and shall be registered on the REWS Public List of Authorised B Electricians. |
|  | Occupational Health & Safety Officer (OHSO) The roles and responsibilities include meeting all the obligations listed in Article 20 of the Special Conditions – Safety on Site, including but not limited to: - Responsible for the Contractor’s compliance with LN281/2004, the Occupational Health and Safety Authority Act (CAP.646), and LN 295/2007 relating to Environmental Management Construction Site Regulations. |  | - Must be registered with OHSA in Malta as a competent person - Holds a valid qualification in the administration of First Aid. |
|  | Quantity Surveyor The following are the minimum responsibilities: - to take measurements of works executed, - compute and present monthly valuation of works, final accounts, evaluate variation orders, - prepare claims and all other works associated with quantity surveying. |  | - Recognised qualification in Quantity Surveying. |
|  | Subcontractors |  |  |
|  | - The Contractor shall be directly and solely responsible for any sub-Contractor on-site or otherwise when carrying out and performing the execution of the Works or part thereof. The Contractor shall supervise and co-ordinate with all sub-Contractors to integrate all activities with the remainder of the work. For the purposes of this contract any sub-Contractor will be treated as employees of the Contractor in all respects. |  |  |
|  | Co-Operation and Co-ordination with other Contractors |  |  |
|  | - The Contractor shall carry out the Works in such manner that will provide full co-operation and coordination with other Contractors employed on the site and shall ensure that his Performance Programme fits with the programme of works of these Contractors, in accordance with the sequence of works specified in the Contract drawings. The Contractor shall not unnecessarily cause delay or restrict access to other Contractors due to his activities and shall allow for the coordination of works with other Contractors and the general attendance of one Contractor upon another. |  |  |
|  | Surveys and Shop Drawings |  |  |
|  | - The Contractor is required to conduct a thorough survey of each specific work area well in advance to confirm whether the structure and conditions align with those outlined in the relevant contract drawings or drawings provided by the CA Supervisor and/or representative. If there are any deviations or issues that may impede the Contractor from executing the works as per the specified drawings, the Contractor must create a detailed drawing based on their survey. This drawing should clearly identify any variances or disparities from the design drawings and propose an alternative approach to carry out the work as necessary. |  |  |
|  | ### PAINT |  |  |
|  | General Requirements |  |  |
|  | - Chosen paint must be suitable for interior use. - Allows passage of water vapor, but is water resistant - Resistant to wet scrubbing, easy to clean - Non-yellowing - Almost odourless - Anti-fungal |  |  |
|  | Colour and Appearance |  |  |
|  | - Wall colour to be as specified in the technical drawings, subject to approved samples. The Architect in Charge reserves the right to change the colour at his/her discretion. - Contractor is to provide samples if requested by the architect in charge and approved prior to procurement. - Finish to be matt. |  |  |
|  | Specifications at 20°C |  |  |
|  | - Mass density: approx. 1.5g/cm³ - Solid contents by volume: Approx. 38% - Recommended dry film thickness: 35μm per coat - Practical spreading rate: 8 - 9 m²/lt - Drying time (dust dry): 15 minutes - Minimum interval before over-coating: 3 hours |  |  |
|  | Application |  |  |
|  | - To be applied in at least two coats. - Airless Spray Application: - Recommended thinner: Water - Volume of thinner: 0 – 10 % - Nozzle orifice 0.46 – 0.53mm (= 0.018 – 0.021 inch) - Nozzle pressure: 16.5 MPa (= approx. 165 atm or 2300 psi) - Airspray Application: - Recommended thinner: Water - Volume of thinner: 0 – 15 % - Nozzle orifice: 0.3 - 0.4 MPa (= approx. 3 – 4 atm or 43 – 57 psi) - Roller / Brush Application - Recommended thinner: Water - Volume of thinner: 0 – 5 % - Cleaning Solvent: Water |  |  |
|  | Green Public Procurement |  |  |
|  | Paint Formulation |  |  |
|  | White pigment content - Paints shall have a white pigment content (white inorganic pigments with a refractive index higher than 1,8 per m2 of dry film equal to or lower than: - 38g/m2 for indoor paints, with the exception of indoor wall paints claiming Class 1 wet scrub resistance (WSR) for which 40g/m2 shall apply - 40g/m2 for all outdoor paints. - Undercoats and primers shall have a white pigment content (white inorganic pigments with a refractive index higher than 1,8 per m2 of dry film to or lower than 25g/m2 |  |  |
|  | Verification: | The tenderer shall provide either: - a calculation of the VOC content, supported, if available, by Safety Data Sheets or - A test report carried out according to ISO 11890-2. Products with a VOC content lower than 1.0g/l shall be tested according to IS 17895 Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply. |  |
|  | Content of Volatile Organic Compounds The maximum content of Volatile Organic Compounds (VOCs) shall not exceed the limits given in the Table below. The content of VOCs shall be determined for the ready-to-use product and shall include any recommended additions prior to application such as colourants and/or thinners. Product description (with subcategory denotation according to Directive 2004/CE/42); VOC Limits (g/l incl. water). Interior matt walls and ceilings (Gloss <25@60°); 15. Interior glossy walls and ceilings (Gloss >25@60°) 60; 60. Exterior walls of mineral substrate; 30. Interior/Exterior trim and cladding paints for wood and metal; 90. Interior trim varnishes and woodstains, including opaque woodstains; 75. Exterior trim varnishes and woodstains, including opaque woodstains; 90. Interior and Exterior minimal build woodstains; 75. Binding primers; 15. One-pack performance coatings; 15. Two-pack reactive performance coatings for specific end use such as floors; 100. Decorative effect coatings; 100. Anti-rust paints; 90. |
|  | Verification: | The tenderer shall provide either: - a calculation of the VOC content, supported, if available, by Safety Data Sheets or - A test report carried out according to ISO 11890-2. Products with a VOC content lower than 1.0g/l shall be tested according to IS 17895 Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply. |  |
|  | Product hazard labelling The final product shall not be classified as being acutely toxic, a specific target organ toxicant, carcinogenic, mutagenic or toxic for reproduction, hazardous to the environment, in accordance with Regulation (EC) No 1272/2008 (CLP Regulation), as indicated in Table 3. Acute Toxicity; Acute Tox. 1 Acute Tox. 2 Acute Tox. 3. Specific target organic toxicity – repeated exposure Specific target organ toxicity – single exposure; STOT RE 1 or 2 STOT SE 1, 2 or 3. Carcinogenicity; Carc. 1A Carc. 1B Carc. 2. Germ cell mutagenicity; Muta. 1A Muta. 1B Muta. 2. Reproductive toxicity; Repr. 1A Repr. 1B Repr. 2. Hazardous to the aquatic environment; Aquatic Acute 1 Aquatic Chronic 1 or 2. |
|  | Verification: | - The tenderer shall provide appropriate documentation confirming that the products to be supplied are not classified with the listed hazards. - The documentation of the mixture classification shall be provided in accordance with the rules provided in Regulation (EC) No 1272/2008 (CLP Regulation) and/or Safety Data Sheets. - Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply |  |
|  | Hazardous ingredients The paint shall be compliant with the restrictions presented in Table 5, which either restrict the presence of or limit the concentration of the indicated hazardous substances in the paint. Table 5 Paint hazardous ingredient requirements: Ingredient; Restriction or upper concentration limit. Preservatives:; Preservatives shall be non bio-accumulative1.. Dry film preservatives:; Dry film preservatives shall not be intentionally used with the exception of: - Indoor paints specifically required for high humidity areas with an upper concentration limit of 0.10% w/w - Outdoor paints with an upper concentration limit of 0.30% w/w. Alkylphenolethoxylates: Alkylphenolethoxylates (APEOs) and their derivatives shall not be used in any paint or varnish preparations or formulations.; Shall not be intentionally used.. Phthalates: Phthalates2 identified as substances of very high concern and listed in the candidate list of the REACH Regulation3 shall not be present in any paint or varnish preparations or formulations thereof.. Formaldehyde:; 0.010% w/w. Formaldehyde: Free formaldehyde in the white base, tinting base and colour tint2:. Metals: Cadmium, lead, chromium VI, mercury, arsenic, selenium.; 0.010% w/w per metal or metallic complex/salt, as appropriate. 1 An ingredient is considered bio-accumulative when Log Kow ≤ 4.0 or bio-concentration factor (BCF) ≤ 500. 2 In the case that a wide range of colour tints are to be used the bidder shall indicate which colour tint has the highest potential for formaldehyde release. A test report shall then only be requested for this tint. |
|  | Verification: | The tenderer shall provide appropriate documentation confirming compliance with the criterion, namely: - for preservatives and APEOs: Safety Data Sheets for the product mixture. - for phthalates: Safety Data Sheets for the product mixture. - additionally for preservatives: a test report using OECD 305 Test Guideline can be used as an alternative to the Safety Data Sheet for the sole purpose of confirming that the preservatives used are non-bio-accumulative. - for formaldehyde: a test report based on the Merckoquant method or high-performance liquid chromatography (HPLC) method (See Annex 2), - for metals: a test report based on ISO 3856 series or equivalent. Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply. |  |
|  | Spreading rate The paint shall achieve an efficient spreading rate according to the applicable performance requirement in Table 7. Table 7 Spreading rates for specific paint products: Type of paint; Spreading rate1 (m2/l). White paints and light-coloured paints (including finishes and intermediates); - indoor: 8 - outdoor: 6 - indoor & outdoor: 8. Tinting systems2; 8. Primers and undercoats. a. opaque; 8. b. with specific blocking/sealing, penetrating/binding properties; 6. c. with special adhesion properties; 6. Thick decorative coatings; 1m2 per kg of product. Elastomeric outdoor paints; 4. Notes: 1 The spreading rates apply at a hiding power of 98% 2 Only base should be tested |
|  | Verification: | The tender shall provide a test report using the following methods, or their equivalent: - ISO 6504/1 (Paints and varnishes — determination of hiding power — Part - 1: Kubelka-Munk method for white and light-coloured paints); - ISO 6504/3 (Part 3: determination of contrast ratio (opacity) of light-coloured paints at a fixed spreading rate); - NF T 30 073 for paints specially designed to give a three-dimensional decorative effect or which are characterised by a very thick coat. Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply. |  |
|  | Weathering resistance (only outdoor paints) Masonry, wood and metal paints shall demonstrate resistance to the possible forms of weathering-induced deterioration in Table 8. Masonry paints shall be exposed to artificial test conditions for 1000 hours, wood and metal paints for 500 hours. This shall be demonstrated according to the recommended test methods, or their equivalent, under artificial weathering conditions. Corrosion resistance for metal paints shall also include blistering. Tests should be performed on the tinting base. Table 8 Weathering resistance tests Weathering induced deterioration; Performance requirement; Recommended test. Decrease of gloss1; Less than or equal to 30% of its initial value; ISO 2813. Chalking; 1,5 or better (0,5 or 1,0); EN ISO 4628-6. Flaking; Flake density 2 or less, flake size 2 or less; ISO 4628-5. Cracking; Crack quantity 2 or less, crack size 3 or less; ISO 4628-4. Blistering; Blister density 3 or less, blister size 3 or less.; ISO 4628-2. Corrosion2; Rusting equal to or better than Ri2; ISO 4628-3. 1 Not applicable to mid-sheen and matt-finishes (refer to Annex 1 for details). 2 For anti-rust paints |
|  | Verification: | The tenderer shall provide test results demonstrating performance of the paint according to the requirements listed in Table 8. With the exception of corrosion for metal paints the artificial weathering conditions shall reflect the conditions described in ISO 11507 or (for outdoor wood finishes) QUV accelerated weathering apparatus with cyclic exposure with UV(A) radiation and spraying according to EN 927-6 or their equivalent. For corrosion the relevant atmospheric corrosivity categories in EN ISO 12944-2 and the accompanying procedures specified in EN ISO 12944-6, or equivalent, shall be used. Anti-rust paints for steel substrates shall be tested after 240h salt spray following ISO 9227 or equivalent. Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply with the above criteria. |  |
|  | Fungal and algal resistance of the film (only outdoor paints) (For applications where fungal and algal resistance of the film are needed) Base paints used for exterior masonry and wood and for which fungal and/or algal resistant properties are needed should meet the requirements in Table 9. Table 9 Fungal and algal resistance requirements: Application; Fungal resistance; Algal resistance. Masonry; Class 1 or lower; Score of 0. Wood; Class 1 or lower; Score of 0. |
|  | Verification: | The tenderer shall provide test results demonstrating compliance according to the test methods EN 15457 and/ or EN 15458, or their equivalent. For coatings containing encapsulated dry-film biocides altered conditioning protocols shall also be accepted. Manufacturers shall provide information about any variation in conditioning along with test results of the EN 15457 and/or 15458 standards. Products which have been awarded the EU Ecolabel for paints and varnishes, as established in Commission Decision (EU) 2014/312/EU are deemed to comply. |  |
|  | Management of waste and unused paint The tenderer shall submit a waste management plan for paint leftover from the preparation of the substrate and application. The plan shall include: - Where paint removal/demarking needs to be conducted, an assessment of the potential hazardous content of paint that has been stripped from substrates and, if a risk is identified, a method statement for mitigating the risk by safe handling and disposal. - A method statement for on-site practices for the cleaning of painting equipment and the storage of waste and unused paint for safe disposal as hazardous waste. Measures to minimise waste and unused paint. |  |  |
|  | Verification: | The tenderer shall provide a documented waste management plan which shall include method statements for safe paint stripping, equipment cleaning and waste and unused paint handling and disposal, as well as the measures applied to minimise waste and unused paint. |  |
|  | ### GYPSUM SOFFIT PANNELS |  |  |
|  | General Requirements |  |  |
|  | - Supply and install in place suspended ceiling, composed of a metal structure and 600 x 600mm removable gypsum panels, as per technical drawings and specifications. The ceiling structure shall allow for the installation of 600 x 600mm LED panels (as per technical specifications). Contractor shall allow for application of 2 coats of proprietary paint to the gypsum panels, colour to be confirmed by the Project Supervisor prior to order. - Any visible substructure between the soffit tiles must be in the same colour to ensure a continuous look. - Contractor must take care of installing the soffit panel lighting as per technical drawings and specifications. |  |  |
|  | ### PARTITIONS |  |  |
|  | - Supply all necessary materials and tools to construct plasterboard partitions as per tender specifications and drawings. Where marked on plans and as indicated by the Architect in Charge, boards shall be moisture-resistant and suitable for wet environments. |  |  |
|  | General Requirements |  |  |
|  | - Unless otherwise stated, the partition build-up is to be considered as having a single 12.5mm proprietary plasterboard sheet. - Where necessary, and as per drawings and indication by the Architect in Charge, 12-19mm plywood shall be installed behind the plasterboard lining as reinforcement for any possible fixtures, including but not limited to: lighting, sanitary ware, decorations and hanging furniture. - Allow for a sound insulation layer to achieve the required acoustic performance. - The system, including the framework and the sound insulation layer shall achieve the performance characteristics listed above. Specifications of the sound insulation layer shall be provided by the contractor and approved by the contracting authority prior to order. - Allow for additional stud build-up to accommodate door jambs and architectural features where indicated - Allow for interfaces, joints and shadow gap profiles as per tender drawings. - All screws and fixings to be concealed, grade 304 stainless steel. - Allow for the fixing to ground (concrete, hardstone paving, ceramic tiles) by means of studs and proprietary adhesive as specified by manufacturer. |  |  |
|  | Performance Characteristics |  |  |
|  | - Product to EN 520: 2004, A1 2009 (or equivalent) - Plasterboard shall be prepared to receive plastering, rendering and other finishes as specified in the tender specifications and drawings. - Fire test performance to BS 476: Part 6,7 (or equivalent) - Thermal performance as per Fire Strategy Report - Minimum noise reduction index: 35dB (minimum) to ISO 140-3 (or equivalent) - Strength grade to BS 5234-2 (or equivalent) |  |  |
|  | Fixing to metal framing/furrings |  |  |
|  | - Partitions/ Wall linings: Fix securely and firmly at the following centres (maximum): - Single layer boarding: To all framing at 300 mm centres. Reduce to 200 mm centres at external angles. - Multi-layer boarding: Face layer at 300 mm centres, and previous layers around perimeters at 300 mm centres. - Ceilings: 230 mm. Reduce to 150 mm at board ends and at lining perimeters. - Position of screws from edges of boards (minimum): 10 mm. - Screw heads: Set in a depression. Do not break paper or gypsum core. - Allow for fixing to glass (where required), including any fixings to achieve the specified performance characteristics, including but not limited to strength and acoustic performance. Refer to Glazed Partitions specifications. |  |  |
|  | Joints Between Boards |  |  |
|  | - Tapered edged plasterboards: - Bound edges: Lightly butted. - Cut/ unbound edges: 3 mm gap. - Square edged plasterboards: 3 mm gap. - Square edged fibre reinforced gypsum boards: 5 mm gap. |  |  |
|  | Deflection Heads |  |  |
|  | - Fixing boards: Do not fix to head channels. |  |  |
|  | Finish |  |  |
|  | - Seamless jointing and skim coat plaster - Primer/sealer as recommended by board manufacturer for vapour control - Rendering: as recommended by board manufacturer, three (3) coats shall be applied - Colour of rendering: as per tender drawings, to be confirmed/approved by the architect in charge prior to ordering the material. |  |  |
|  | ### ALUMINIUM APERTURES |  |  |
|  | General Requirements |  |  |
|  | - Supply and install toughened double glazing aperture, including aluminium framework. - Shop drawings: plans, elevations, sections and details to be provided by the contractor (to manufacturer’s recommendation) and be approved by the Contracting Authority. - Aluminium sections shall be in accordance with BS1474 6060/6063 or equivalent. - The window shall be composed of three sliding panels and shall include security locking mechanism by key. - Finishes shall be in polyester powder coat to BS6496 or equivalent, in white, to be confirmed and approved by the Architect in Charge. - External and internal aluminium glazing beads and flexible gaskets to BS6262 or equivalent and the internal wedge gasket and captive bead gasket shall be high in performance against weathering. - Performance tests shall comply with BS6375 Pt 1 or equivalent. - Glazing must be wind and watertight under all conditions with full allowance made for deflection and other movements. Dimensional tolerances of glass panels shall be within +/- 2mm of specified dimensions. - All aluminium profiles and glass panels shall be clean and free from obvious scratches, bubbles, cracks, rippling, dimples and other effects. - Edges shall be undamaged. Shells and chips shall not be more than 2mm deep and extending not more than 5mm across the surface. - Rubber gaskets and other necessary measures shall be taken in order to minimize sound leakage |  |  |
|  | Performance Characteristics |  |  |
|  | - Fire resistance to BS 476-22 (or equivalent) - Fire propagation to BS 476-6 (or equivalent) - Spread of flame to BS 476-7 (or equivalent) - Acoustic insulation to BS EN ISO 10140-2(2010) (or equivalent), minimum: 40dB(Rw) - Strength to BS 5232-2 grade (or equivalent), structural tests in accordance with BS 5234-2 (or equivalent) - Safety to BS EN 12600 (or equivalent) |  |  |
|  | Dimensions |  |  |
|  | - Height and width of panels and thickness of aluminium frame: as per drawings, to be confirmed upon on-site measurement by the contractor - Thickness of each glass pane shall not be less than 6mm (refer to performance characteristics) - Spread of flame to BS 476-7 (or equivalent) |  |  |
|  | ### PAINTING WORKS |  |  |
|  | General |  |  |
|  | - Where applicable, a coat of water-repellent primer must be applied for protection, before the application of render, in all external areas and areas which are susceptible to deterioration. - Renders shall comply with BS EN 13914 – Design, preparation and application of external rendering and internal plastering (or equivalent standards). - A three (3) year guarantee shall be specified on all rendering works - All colours and finishes are to be selected or approved by the Architect-in-Charge and provision must be made for the execution of trial areas on the site as required. - Thinning of materials where necessary shall be carried out with the type of thinner in proportions recommended by the Manufacturer of the paint. |  |  |
|  | Approval of Materials |  |  |
|  | - Prior to use, all materials are to be approved by the Architect-in-Charge or his representative. The Contractor shall ensure compatibility of proposed materials for intended use. - All painting material described in the Specifications shall comply with BS 6150:2006+A1:2014 and they must be to the satisfaction of the Architect-in-Charge who might request samples prior to the execution of works. |  |  |
|  | Substrates |  |  |
|  | - Existing substrates to be rendered shall be sound, free from loose areas and significant cracks or gaps, free from deteriorating, damp or unsuitable material, cleaned of loose mortar, fins, grease, dirt, efflorescence, mould or dust. - All cutting, chasing, making good, fixing of conduits and surface outlets shall be completed. Surface flatness/regularity shall be within the specified tolerance limits. - Existing substrate surfaces, and rendered surfaces to receive further coats of rendering, shall have an appropriately rough surface to achieve a good key. The surfaces shall be open textured, scratched or nail-floated, and shall be sufficiently mature before a subsequent layer is applied. - Surfaces composed of natural franka stone shall be preliminary treated with a proprietary sealer as per section 1.1 of this document. - Dubbing out shall be used to correct substrate inaccuracies. Dubbing out in smooth dense concrete shall be prohibited. The thickness of any dubbing coat shall not exceed 16mm, and the maximum overall thickness of any dubbing shall not exceed 20mm. The dubbing coat shall be mixed as an undercoat and shall be applied to achieve a firm bond. Each dubbing coat shall be allowed to set sufficiently before the next coat is applied. The surface of each coat shall be cross-scratched or combed to provide a good key. - Services chased into the substrate shall be isolated from the coating by covering with metal lathing fixed at staggered centres along both edges, to prevent cracking over conduits and other services. - Substrate shall be damped down, just sufficiently to ensure uniform absorption, before the first coat is applied and as the work proceeds. Rendering in areas subjected to prolonged direct sunlight shall be avoided. Scaffolding works shall be erected such that there are no putlog holes and other breaks in render coats. |  |  |
|  | Painting for internal walls and ceilings |  |  |
|  | - The paint shall comply with EN 13300, Paints and Varnishes, Water-borne Coating Systems for Internal Walls and Ceilings. The paint shall comply with the ecological and performance criteria adopted by the EU for the award of the Eco-Label for internal paints and varnishes. - All internal walls and ceilings shall be finished with one coat undercoat and two finishing coats of matte plastic emulsion paint with anti-fungal additives. Colour shall be approved by the Architect-in-Charge. |  |  |
|  | ### MASONRY WORKS |  |  |
|  | General Requirements |  |  |
|  | - The standard of workmanship shall be in accordance with the relevant clauses of BS 8110, provided that the relevant clauses of any subsequent EN Codes of practice shall take precedence if available. Standards of workmanship shall comply with any and all statutory requirements. - Proprietary products and materials shall be used in accordance with the Manufacturer’s written instructions. - Upon site delivery, the masonry shall be checked to ensure that: - They are undamaged or have chipped edges and corners - Of the specified dimensions and geometry - Worked so that the material bed is normal to the load - Worked so that joints are at right angles to the pressure exerted - Masonry shall be kept dry, handled by hand or tackle, crane and other suitable mechanical aids. |  |  |
|  | Staggered Courses |  |  |
|  | - Joints shall be staggered from one course to the next, with vertical joints displaced by approximately half the length of a building unit between one course and the one above. |  |  |
|  | Footing and Course Height |  |  |
|  | - Where a new structure is to be tied to a part of the existing structure, a minimum footing of not less than 100mm is to be provided at every alternate course. Course heights of any new structures are to be matched with those of the existing structure to which they are tied. Walls at right angles to one another shall be properly bonded by forming toothings in every alternate course. |  |  |
|  | Mortar Joints |  |  |
|  | - Mortar between masonry units shall be laid in a uniform continuous pile along the whole horizontal length of the building unit in the case of franka masonry and in a uniform continuous pile along the whole horizontal edge of the brick in the case of concrete brickwork, so as to ensure a continuous unbroken horizontal mortar joint. Similarly, vertical joints shall be made up of a continuous layer of mortar between adjacent units. The practice of placing of individual piles of mortar at either end of the horizontal surface of the (franka) unit or along part of the outer edge (concrete brickwork) or along only a portion of the vertical face shall not be accepted. |  |  |
|  | Mortar for Construction |  |  |
|  | - Mortar used in construction shall have a mix proportion of 1 part of cement to four parts aggregate by volume. Aggregate shall be made up of fine sand (ramel fin) and limestone dust (xahx tal-inġara) in the proportion of one part of sand to two parts limestone dust by volume. Water content in the mortar mix shall be kept to the minimum necessary to allow workability and in general should preferably not exceed three quarters (75%) of the cement content by volume. - Mortar shall be mixed using fresh dry ingredients, first mixed dry with the water added later and re-mixed to a uniform consistency. Mortar batches shall be used within half an hour of being mixed. Partially-set mortar or mortar which exceeds its usable time shall be discarded. Addition of discarded mortar materials into fresh mixes shall not be allowed. - Mortar mixed for use in limestone construction that is to be left in its natural exposed finish shall have its ordinary Portland cement component substituted with one part white cement (siment abjad) and one part lime (ġir). |  |  |
|  | Pointing Mortar |  |  |
|  | - Mortar to be used for pointing of exposed natural limestone shall be made up of one part white cement and one part lime to four parts limestone dust (xaħx tal-inġara) and two parts fine sand. |  |  |
|  | Stone Masonry |  |  |
|  | - Limestone blocks shall be of the best quality and shall be obtained from approved sources. These shall be free from all defects, including but not limited to, blue markings (swaba), any defects on the exposed face or chipped corners and edges. The Architect-in-Charge shall have the right to reject defective limestone or instruct the Contractor to remove and replace such work at the Contractor’s sole expense. - Cutting into masonry walls shall be subject to the following conditions: - Cutting shall be delayed until the mortar has hardened - Approval from the Architect-in-Charge shall be obtained prior to cutting into load-bearing walls - Approval from the Architect-in-Charge shall be obtained prior to cutting holes greater than 300mm square - Cuttings shall be performed in a manner that involves minimal vibration to the wall - No chasing shall occur in walls less than 75mm thick - In solid walls, no chasing shall occur deeper than one-sixth the wall’s thickness at any point when horizontal, or one-third at any point when vertical - No chases shall be allowed back-to-back in any wall - All the chases required for the fixings of other components shall be cut as directed by the Architect-in-Charge. |  |  |
|  | ### FORMWORK |  |  |
|  | Standards |  |  |
|  | - Design and construction of falsework and formwork shall be in accordance with the following where applicable: - BS 5975:2008 Code of practice for falsework - Formwork: a guide to good practice (Concrete Society, second edition1995) - CIRIA Report 136 Formwork striking times - criteria, prediction and methods of assessment (CIRIA, 1995) - BS 8110:1997 Structural use of concrete. Part 1 Code of practice for design and construction - BS 6349:2000 Maritime Structures. Part 1 Code of practice for general criteria |  |  |
|  | Types of Material |  |  |
|  | - Formwork materials shall suit the method of construction to be used and the surface finish required for the final work. - Permanent formwork may be used subject to the agreement of the Architect-in-Charge. |  |  |
|  | Release Agents |  |  |
|  | - The Contractor shall choose release agents to suit the method of construction and the finish required, and shall take note of the requirements of subsequent trades. - All release agents used shall be non-staining, non-injurious to the finished concrete and shall not be adversely affected by the weather. |  |  |
|  | Formwork Use |  |  |
|  | - Formwork shall be constructed so as to contain the concrete, to give the required surface finish to the concrete and to adequately support the concrete in the desired final position throughout the period of use. - Where structural concrete relies on permanent or temporary support from the ground, the Contractor shall ensure that the support is adequate for concrete operations. - Formwork shall be clean and clear of all debris, free water and ice before concrete is placed. - Concrete shall not be cast directly against existing construction or faces of excavations without the prior agreement of the Architect-in-Charge |  |  |
|  | Block-Outs and Cast-In Items |  |  |
|  | - The Contractor shall set-out and fix all cast-in items shown or referenced on the drawings. Any clashes between holes, cast-in items and reinforcement shall be resolved before any concrete is placed. The Contractor shall clear out block-out items after concreting. |  |  |
|  | Formwork Ties |  |  |
|  | - Through-ties may be used to support vertical faces of formwork, except in cases of water-resisting construction. - Non-ferrous metal shall be left in the concrete cover zone when formwork has been struck. - The Contractor shall make good any holes left exposed to view in the faces of the concrete to the agreement of the Architect-in-Charge. |  |  |
|  | Striking |  |  |
|  | - The concrete shall be supported in the required position until it has adequate strength, as determined by the Contractor, to support its own weight and any construction loads, without short-term or long-term distress. - Formwork may be struck at a time determined by the Contractor, noting the ambient conditions at the time of removal, the concrete’s strength, and any methods for curing and protecting the newly-exposed concrete. - Formwork shall be removed carefully to avoid damaging the concrete surface. Any damage so caused shall be made good by the Contractor to the acceptance of the Architect-in-Charge. - The exact sequence of propping/re-propping and back-propping through the structure shall be set out in a method statement prepared by the Contractor, shall be agreed with the Architect-in-Charge in advance, and shall have no damaging effect on the permanent structure. |  |  |
|  | Construction Joints and Pour Sizes |  |  |
|  | - The Contractor shall position and form construction joints to suit the structure and so as not to cause any short-term or long-term distress to the structure in accordance with the instructions of the Architect-in-Charge. - The Contractor shall carefully-prepare construction joint surfaces to expose the coarse aggregate to provide good key. The method for carrying this out shall be as approved by the Architect-in-Charge. - Pour sizes, except as agreed otherwise between the Contractor and Architect-in-Charge, shall be as shown as in Table 1 below. |  |  |
|  | Infilling of Hollow Concrete Blocks |  |  |
|  | - In the event that filling of brickwork is required, this shall take place every four courses with the top most course left short so as to provide a key for the next pour. |  |  |
|  | ### REINFORCEMENT |  |  |
|  | General Materials |  |  |
|  | - All reinforcement shall comply with the requirements of BS 6349 Part 1:2000 Clause 58.4.7, BS 4449:2005+A2:2009, BS 4482:2005, BS 4483:2005, BS 8666:2005 as appropriate. Reinforcement in accordance with BS 4449:2005 shall be ductility class B. |  |  |
|  | Reinforcement Supply and Testing |  |  |
|  | - The Contractor shall submit details of the source of all reinforcement to be used. - All reinforcement shall be delivered in clearly identified, tagged bundles, mats or prefabricated assemblies and shall be stored on site in a manner so as not to be contaminated or otherwise damaged. Fabric shall be stored flat. - Reinforcement shall not be dropped from a height, mechanically damaged or shock-loaded in any way. |  |  |
|  | Spacers |  |  |
|  | - The Contractor shall detail, supply and fix all spacers. The materials and workmanship shall be in accordance with BS 8110: Part 1: 1997, Clause 7.3 and BS 7973:2001 Spacers and chairs for steel reinforcement and their specification. The Contractor shall ensure that the spacers have the required performance characteristics. - In exposed finish work the type of spacer used shall be agreed with the Architect-in-Charge before any work is started. |  |  |
|  | Couplers |  |  |
|  | - The Contractor shall submit details of the source and suppliers to the Architect-in-Charge for agreement. - All manufacturers/suppliers shall be registered members of the UK CARES Quality Assurance scheme or equivalent unless agreed otherwise by the Architect-in-Charge. |  |  |
|  | Continuity Strips |  |  |
|  | - Proprietary continuity strips can be used subject to agreement by the Architect-in-Charge. |  |  |
|  | Reinforcement Protection Coat |  |  |
|  | - If required, the Contractor is to seek approval from the Architect-in-Charge for the use of anti-corrosive cement based, polymer-modified coating for steel reinforcement bars. This shall be used to block reinforcement corrosion resulting from carbonation or chloride ingress. The Contractor is to ensure that the chosen product is fully-compatible with subsequent build-up layers. |  |  |
|  | General Workmanship |  |  |
|  | - At the time of placing concrete, reinforcement shall be clean, free of corrosive pitting, loose rust and mill scale and other substances that may adversely affect bonding with concrete. Light surface rust will be accepted. - All cutting, bending and fixing shall be in accordance with BS 6349: Part 1:2000, Clauses 58.4.9 and BS 8110: Part 1: 1997, Clauses 7.2 and 7.3. |  |  |
|  | Tying and Welding |  |  |
|  | - Tying of reinforcement shall be carried out with black annealed mild-steel 16-guage tying wire. All ends shall be bent away from the concrete face and all loose ends shall be removed before placing the concrete. - Welding of reinforcement shall be in accordance with the requirements of BS 8110: Part 1: 1997, Clause 7.6 and BS EN ISO 17660-1:2006, BS EN ISO 17660-2:2006 Specification for metal arc welding of steel for concrete reinforcement. Welding procedures and welder qualifications shall be subject to the agreement of the Architect-in-Charge. |  |  |
|  | Projecting Reinforcement |  |  |
|  | - All reinforcement ends left projecting from cast concrete shall be free of release agents and shall be protected against damage and corrosion, although light surface rusting will be accepted. |  |  |
|  | ### CONCRETING |  |  |
|  | Placing and Compaction |  |  |
|  | - Above water level, concrete shall be placed and compacted in the structure in accordance with BS EN 1992-1-1:2004. - Concrete shall be placed and fully-compacted with the appropriate vibrator equipment so as to avoid cold joints and honeycombing, and to minimise segregation, excessive blemishes or other defects in the hardened concrete. - Kickerless construction shall be in accordance with Kickerless construction (British Cement Association, 1996). Where kickers are used, they shall be monolithic with the slab, of sound construction and at least 100mm high. - Should premature stoppage of a pour occur, the Contractor and Architect-in-Charge shall agree on the extent and timing of any necessary remedial work before resumption. |  |  |
|  | Concreting in Extreme Weather |  |  |
|  | - For concreting in cold weather, the recommendations of BS EN 1992-1-1:2004, shall be followed and further guidance may be found in BS 8500-2:2015. - For concreting in hot weather the recommendations of BS EN 1992-1-1:2004, shall be followed and further guidance may be found in BS 8500-2:2015. |  |  |
|  | Curing |  |  |
|  | - The surface of the concrete shall be cured to avoid premature drying out. Methods of curing and curing periods shall be in accordance with BS EN 1992-1-1:2004, and as agreed with the Architect-in-Charge. Curing membranes shall be compatible with any finishes to be applied subsequently. |  |  |
|  | Protection |  |  |
|  | - All surfaces shall be protected from the effects of adverse weather in accordance with BS EN 1992-1-1:2004. The structure shall be protected against damage. - Damage occurring shall be made good by the Contractor. Methods to be used shall be proposed by the Contractor for agreement with the Architect-in-Charge. - The faces of cast concrete that will be visible in the completed structure shall be protected from rust staining. - If concrete is to be placed in a large volume pour, if a rich concrete is used or if the section is thicker than 500mm, consideration shall be given to the concrete temperature rise above ambient and to reducing the risk of early thermal cracking. - Where a risk of thermal cracking is identified, the location of temperature monitoring apparatus and interpretation of the temperatures recorded shall be agreed with the Architect-in-Charge prior to installation. |  |  |
|  | Conformity and Identity Testing During Concreting Operations |  |  |
|  | - The Contractor shall prepare three cubes from every pour (structural concrete only) and shall be retained on site by the Supervisor in a secure place under optimal curing condition during the 28 days curing stage. - The Contractor shall inform the Architect-in-Charge at least 24 hours before concrete laying works occur. |  |  |
|  | Inspection before Casting |  |  |
|  | - The Contractor shall inspect the formwork, spacers, fixed reinforcement and inserts before casting the concrete and shall only allow concrete to be cast once the work is satisfactory and the Architect-in-Charge has had reasonable opportunity for inspection. |  |  |
|  | Inspection after Placing |  |  |
|  | - After the specified period of curing, the Contractor shall inspect the relevant work. If any remedial measures are necessary, the Contractor shall submit details to the Architect-in-Charge for agreement. - In water-resisting construction, inspection to identify defects which may lead to water penetration shall be carried out jointly between the Contractor and Architect-in-Charge before backfilling or covering up. Further inspection shall be jointly carried out to identify any water penetration after backfilling. - Any leaks or damp patches shall be repaired by methods proposed by the Contractor and agreed with the Architect-in-Charge, in accordance with BS 8102: 2009, and BS 8215:1991. |  |  |
|  | Surface Finishes |  |  |
|  | - Concrete finish shall be a standard finish trowelled smooth. - The Contractor shall take all reasonable actions to minimise surface cracking. Unless otherwise specified isolated cracks of width up to 0.3mm will be accepted in localised areas. Cracking that will allow corrosion of reinforcement, unsightliness, unacceptable water leakage, impair durability or reduce structural adequacy shall be rectified by the Contractor as agreed with the Architect-in-Charge. |  |  |
|  | Admixtures |  |  |
|  | - Generally, admixtures should conform to BS EN 934-2. - Admixtures should not impair the durability of the concrete nor combine with the constituents to form harmful compounds nor increase the risk of corrosion of the reinforcement. - Calcium chloride and chloride-based admixtures should never be added to concrete which is to be reinforced, pre-stressed or is to contain embedded metal or cement conforming to BS 915 or to BS 4248. - If two or more admixtures are to be used in the same concrete mix, data should be obtained to assess their interaction and to ensure their compatibility. - Admixtures are permitted in designed and prescribed mixes and, with certain restrictions, in designated mixes but are not permitted in standard mixes. |  |  |
|  | Cover to Reinforcement |  |  |
|  | - Cover to reinforcement shall be in accordance to detail drawings prepared by the contractor’s Perit key expert, taking into account the proximity of the building to the sea. |  |  |
|  | ### CONSOLIDANT/SEALER |  |  |
|  | - The product shall be breathable and adequate for application on limestone - The product shall be colourless and shall ensure that there is no discolouration to the stone - The product shall be ammonium oxalate/ethyl silicate, subject to approval by the Architect in Charge prior to the commencement of works. - Water absorption coefficient: <7.5% to EN 1504-2/ EN 13580:2002 (or equivalent standard) - Alkali resistance: <10% to EN 1504-2/ EN 13580:2002 (or equivalent standard) - Penetration depth: >5mm to BS EN 14630:2006 (or equivalent standard) |  |  |
|  | ### VINYL FLOORING/WALLS |  |  |
|  | General Description |  |  |
|  | - Provide and install homogeneous vinyl floor and wall covering with Class 34 classification (heavy duty), suitable for commercial use. The winning bidder has the option to provide this material in either rolls or tiles, subject to being in line with the provided technical specifications. It is the responsibility of the winning bidder to take any necessary measures to prepare the sub-base for installation as per manufacturer’s guidelines. |  |  |
|  | Standards and Compliance |  |  |
|  | - The flooring shall comply with the following standards: - ISO 10581 – Homogeneous vinyl floor covering (Type I) - EN 14041 – CE Marking and Declaration of Performance - EN 13501-1 – Reaction to fire classification - ISO 14644-1 – Cleanroom classification (ISO Class 4) - Fire classification: Bfl-s1 - Critical radiant flux: ≥ 8 kW/m² - Ignitability: Pass (EN ISO 11925-2) - Slip resistance (EN 13893): Class DS (μ ≥ 0.30) - Slip resistance (DIN 51130): R9 - Pendulum test (BS 7976-2): Low risk of slip |  |  |
|  | Material Characteristics |  |  |
|  | - Surface treatment: Polyurethane (PUR) reinforced surface - Surface restoration: Fully restorable without wax - Total thickness: 2.0 mm (Tolerance: +/- 5%) - Wear layer: 2.0 mm (full thickness homogeneous) - Total weight: 2750 g/m² (Tolerance: +/- 5%) |  |  |
|  | Physical and Mechanical Performance |  |  |
|  | - Residual indentation: ≤ 0.10 mm (typical 0.02 mm) - Dimensional stability: - Tiles: ≤ 0.25% - Rolls: ≤ 0.40% - Curl resistance: - Rolls: ≤ 8 mm - Tiles: ≤ 2 mm - Seam strength: ≥ 400 N / 50 mm - Castor chair resistance: Suitable for continuous use - Chemical resistance: Excellent - Bacterial resistance: Does not promote growth - Decontamination: Excellent (ISO 8690 / DIN 25415) - Wetroom suitability: Watertight (EN 13553 Annex A) |  |  |
|  | Special Performance Requirements |  |  |
|  | - Cleanroom suitability: ISO Class 4 - Riboflavin test: Class 0 (Excellent) - Marine certification: IMO FTP Code compliant |  |  |
|  | Dimensions and Finishes |  |  |
|  | - Rolls indicative dimensions: 2.0 m width x 25 m length - Tiles: 600 x 600 mm (tolerance +/- 10%) - Finish: indicative finish shall be light grey with minor colour variations, subject to approved sample by the contracting authority or its representatives - Flooring shall be capable of dry polishing restoration without the need for wax or polish |  |  |
|  | Skirting |  |  |
|  | - Skirting shall be in line with the technical specifications above, or as recommended by the manufacturer. |  |  |
|  | ### INTERNAL DOORS |  |  |
|  | - Shop drawings: plans, elevations, sections and details to be provided by the contractor (to manufacturer’s recommendation) and/or literature or samples to be approved by the Contracting Authority prior to order |  |  |
|  | Dimensions |  |  |
|  | - Refer to tender drawings - Allow for openings of circa 0.95m (h) x 2.1m (h) - Minimum thickness of door: 32mm |  |  |
|  | Material & Finish |  |  |
|  | - Colour: white, subject to approved sample. - Surface to be in semi-matte - Unless otherwise stated, all hardware and fixings shall be in stainless steel |  |  |
|  | Performance Characteristics |  |  |
|  | - Product to EN 520: 2004, A1 2009 (or equivalent) - Plasterboard shall be prepared to receive plastering, rendering and other finishes as specified in the tender specifications and drawings. - Fire rating: 60 minutes - Fire test performance to BS 476: Part 6,7 (or equivalent) - Fire resistance to be tested to BS 476-22, BS EN 1634-1, BS EN 1634-3 (or equivalent) - Thermal performance as per Fire Strategy Report - Minimum noise reduction index: 35dB (minimum) to ISO 140-3 (or equivalent) - Minimum soundproofing index (as tested on site): 35dB to ISO 717-1 (or equivalent) - Strength grade to BS 5234-2 (or equivalent) - Each door shall be equipped with an independent security lock and corresponding key to BS 3621 (or equivalent) - Allow for self-closing mechanism as approved by AIC prior to order/manufacturing. |  |  |
|  | ### INTERNAL & EXTERNAL PLASTERING |  |  |
|  | Scope of works |  |  |
|  | - Rendering in gypsum plaster - Finishing of exposed stone - Rendering in cement-based mix |  |  |
|  | Samples and Documents with Tender Submission |  |  |
|  | The Contractor’s submittals shall be as described in the tender’s Instructions to Tenderer, Technical Specifications. |  |  |
|  | Approval of Materials |  |  |
|  | - The Contractor’s submittals shall be as described in the tender’s Instructions to Tenderer, Technical Specifications. |  |  |
|  | General Workmanship |  |  |
|  | - Comply with BS EN 13914 - Design, preparation and application of external rendering and internal plastering. - A three (3) year guarantee shall be specified on all rendering and plastering works. |  |  |
|  | Supervision |  |  |
|  | - Pre-mixed plaster shall be carried out by experienced applicators. All the workers and Architect-in-Charge staff employed for the work shall be fully-instructed and trained on the method of preparation and application in accordance with the Manufacturer’s recommendations. |  |  |
|  | Handling & Storage |  |  |
|  | - Bagged premix mortar shall be stored separately by types, off the ground in a dry well-ventilated and covered space. Use shall occur in order of delivery and within Manufacturer-recommended time limit. |  |  |
|  | Preliminary Checks |  |  |
|  | - Prior to commencement, it shall be ensured that working conditions are suitable and that the surface to be rendered is clean and dust-free. Furthermore, no water shall be allowed to leak in behind the coating. |  |  |
|  | Access |  |  |
|  | - Ensure provision of step-ladders, towers, etc. Workers are not to stand on finished work and shall not lean equipment against finished work. |  |  |
|  | Masking |  |  |
|  | - Before application of plaster, masking film/tape is to be applied to all joinery, pipes, roofs and all areas likely to be marked by such plaster. Drop cloths and ground covers are to be used to keep the working areas clean. |  |  |
|  | Shade |  |  |
|  | - Plasters are to be applied away from direct sunlight, if necessary using a shade cloth or by working on shaded elevators. |  |  |
|  | Method of Application |  |  |
|  | - The method of application shall be in strict accordance with the Manufacture’s recommendations. - Preparation of surfaces (including hacking, dubbing, cleaning, priming, etc.) - Use and installation of beads - Preparation of mixtures - System application in layers - Application of finishes coats - Curing, cleaning and protection |  |  |
|  | General Quality of Finish |  |  |
|  | - All corners and edges to be straight and true. - Finished surfaces to be perfectly level and plumb. Plastering Contractor must compensate for and correct any deviations from plumb arising from the construction, even in cases of horizontal surfaces such as window sills and lintels. - Finished surfaces to be completely level and uniform in all areas, including areas where there is a change in the nature of the background. The maximum permissible deviation is ±5mm over 4 metres in all directions. |  |  |
|  | Special Considerations |  |  |
|  | - Horizontal DPCs - Fix appropriate edge profile and make provisions to discontinue plastering where any existing horizontal DPCs extend through the plaster. - Movement Joints - Fix appropriate edge profile and make provisions to discontinue plastering where any movement joints are required to extend through the plaster. |  |  |
|  | Removal of Superfluous Accretions |  |  |
|  | - This will include the removal of any metal grilles, wires, rods, nails and other accretions found embedded into the building’s stone. Such metal inserts can damage the stone through rust staining and can also result in a shattered block due to expansion of the iron as it rusts. Any such inserts are to be removed by hand, ensuring elimination of rust residue from the stone. Leftover holes are to be filled in with a lime-based mortar. |  |  |
|  | Removal of Surface Layers |  |  |
|  | - Exposed stone shall be cleaned with a gentle, low-pressure washing technique. Generally, the aim of the cleaning process is to remove accumulation of contaminants from the stone’s surface, whilst retaining its natural patina, texture and profile. Sprayers or sprinklers will be used, together with manual brushing with bristle brushes. Salt-free, preferably distilled or de-ionized water will be used. The use of local tap water is not recommended. - Oil-based paints shall be removed by a neutral paint-remover certified to contain no salts or any other deleterious agent. Repeated applications in paste form might be necessary to remove persistent stains. - Old plasters and similar coatings shall be removed by hand tools using manual methods and constant supervision so as not to damage the stone surface. - Cement pointing and facing shall be removed manually taking care not damage the surrounding weakened stone. - Mechanical means, especially involving the use of power tools (such as rotating-disc cleaners and dry or wet sand-blasters) or tipped metallic tools shall not be permitted unless instructed otherwise by the Architect-in-Charge. |  |  |
|  | Preparation of Masonry Structure for Pointing |  |  |
|  | - If upon further inspection any mortar joints are found to be loose, their cleaning and opening-up will be carried out using hand-held non-powered tools to a minimum depth of 30mm, and never to a depth less than their width. This shall be done without damaging the adjacent masonry. - If the mortar has failed to such an extent that the joints are largely empty, they will be deep-tamped and hand-grouted to the depth required for pointing. - The work shall commence at the top of the wall moving downwards. - A biocide shall be applied prior to flushing out. - Dust and loose debris shall be removed and the joints dampened with clean de-ionised water to control suction as necessary. |  |  |
|  | Cleaning of Organic Growth |  |  |
|  | - Surface soiling by organic growth shall begin removal by simple dry bristle knife blades and spatulas, without damaging or abrading the underlying surface. If such surface is delicate or liable to be marked or scoured in any way, this method will be limited as approved by the Architect-in-Charge. - The application of mild biocides, having a long-term inhibiting effect on re-colonisation, shall follow the initial removal of organic growth. Products to be used shall be methoxytriazine or quaternary-ammonium compounds, or as per Architect-in-Charge’s approval. The biocides shall be applied in strict accordance with their Manufacturer’s recommendations for safety and protection of both workers and environment. - The removal of fungus, lichens and the like will be limited to places where these are causing harm, as approved by the Architect-in-Charge. In an exceptionally dry period, dormant dry lichens shall be revived with light water spraying prior to the application of the biocide. - Application of biocidal treatments will not be undertaken during wet weather or windy conditions leading to excessive drift of spray. - The Contractor shall protect all surfaces that are excluded from chemical cleaning. All chemical agents shall be contained within their respective treatment areas. |  |  |
|  | Pointing in Stone |  |  |
|  | - Portland cement mixes will not be permitted, unless otherwise instructed by the Architect-in-Charge. All mixes shall be lime-based and be compatible with the stonework in colour, strength and permeability. They will also be as close as possible in colour, composition and properties to the original mortars. - The properties of the mix shall be improved if hydraulic lime is used instead of either hydrated lime or pozzolana. In such cases only aggregate shall be added - no cement or other pozzolanic additives shall be necessary. |  |  |
|  | Pointing Methodology |  |  |
|  | - Prior to pointing/re-pointing, all open joints shall be cleaned from dust and loose materials, and the surrounding stones adequately dampened with de-ionised water. All pointing shall be carried out in moist, warm conditions and in layers not exceeding 10mm thickness. - Fresh pointing shall be allowed to dry slowly and be adequately protected from excessive heat and direct sunshine by a tarpaulin, and should occasionally be dampened to avoid cracking. - A minimum of 24 hours shall be permitted between the applications of each layer of pointing. - When laying new stonework, all vertical and horizontal joints shall be adequately buttered with mortar. - After the initial set has taken place, the Contractor shall stipple the joints with a stiff brush to remove laitance/excess fines and achieve a coarse texture. - If the stones have retained sharp edges, joints shall be filled flush unless the original joint face was profiled in some other way. In the case of weathered edges, or where the stone has spalled off, the face of the new mortar shall be kept back such that the apparent joint width does not increase. The required finish shall be as per original surviving masonry and as approved by the Architect-in-Charge. |  |  |
|  | Mortar |  |  |
|  | - The Contractor shall ensure that all mortar joints are built up in layers not exceeding 10mm in thickness or as recommended by the Manufacturer in cases were the use of ready-mixed lime mortars are permitted. - The background shall be thoroughly cleaned to remove all dust and debris and the areas of application shall be dampened to control suction. - The mortar shall be built up and firmly applied in layers until the specified thickness is reached and the Contractor shall ensure good adhesion with no voids. A mechanical key shall be formed to the undercoat/s by combing or scratching so as to produce evenly spaced lines. - Each layer shall be allowed to achieve an initial set prior to the application of subsequent coats, and prevented from drying out too rapidly by covering immediately with plastic sheeting and/or dampening intermittently with clean water. - The finishing mortar joint shall be formed accurately to the required planes/profiles and flush with adjacent masonry, as per Architect-in-Charge instructions. - The Contractor shall provide adequate protection from adverse weather until the mortar repairs have fully set. |  |  |
|  | General Rendering |  |  |
|  | - Mortar for plastering and rendering shall comply with EU Directive 89/106/EEC (or equivalent) as implemented by the relevant decision. - Workmanship shall be in accordance with BS 8000: Part 10: 1989, Workmanship on Building Sites, Plastering and Rendering (or equivalent). - Rendering and Plastering mortar shall comply with EN 998-1 – Classification GP (General Purpose) (or equivalent). |  |  |
|  | Substrates |  |  |
|  | - Existing substrates to be rendered shall be sound, free from loose areas and significant cracks or gaps, free from deteriorating, damp or unsuitable material, cleaned of loose mortar, fins, grease, dirt, efflorescence, mould or dust. - All cutting, chasing, making good, fixing of conduits and surface outlets shall be completed. Surface flatness/regularity shall be within the specified tolerance limits. - Existing substrate surfaces, and rendered surfaces to receive further coats of rendering, shall have an appropriately rough surface to achieve a good key. The surfaces shall be open textured, scratched or nail-floated, and shall be sufficiently mature before a subsequent layer is applied. - Where necessary, surfaces composed of natural franka stone shall be preliminary treated with a proprietary synthetic fixative resin. - Dubbing out shall be used to correct substrate inaccuracies. Dubbing out in smooth dense concrete shall be prohibited. The thickness of any dubbing coat shall not exceed 16mm, and the maximum overall thickness of any dubbing shall not exceed 20mm. The dubbing coat shall be mixed as an undercoat and shall be applied to achieve a firm bond. Each dubbing coat shall be allowed to set sufficiently before the next coat is applied. The surface of each coat shall be cross-scratched or combed to provide a good key. - Services chased into the substrate shall be isolated from the coating by covering with metal lathing fixed at staggered centres along both edges, to prevent cracking over conduits and other services. - Substrate shall be damped down, just sufficiently to ensure uniform absorption, before the first coat is applied and as the work proceeds. Rendering in areas subjected to prolonged direct sunlight shall be avoided. Scaffolding works shall be erected such that there are no putlog holes and other breaks in render coats. - Rendering shall be applied after the installation of sub-frames for the apertures in external walls, and shall be applied flush against such sub-frames. |  |  |
|  | Prescribed Cement-Based Mortar |  |  |
|  | - Prescribed cement-based mortar shall consist of the application of a mortar containing Portland cement and sand, in prescribed proportions, to the external or internal surface of the building, in one or more layers. - The mix proportions for cement-based renderings shall normally conform to BS 5262 (or equivalent), Code of Practice for External Renderings and BS 5492 (or equivalent), Code of Practice for Internal Plastering. - Cement, for use in mortar shall conform to BS EN 197-1 CEM 1/42.5 (or equivalent). - Sand for use in cement based mortar shall comply with BS EN 13139 (or equivalent). Sand shall have a grading characteristic suitable for the required texture. - For the Finishing coat, the grade shall be adjusted to suit the type of finish indicated in the Drawings or BOQ. For smooth, textured finishes, it may be necessary to remove the coarser particles, whilst for the scraped texture finish, a larger proportion of coarser material may be retained. - Water shall be clean and fresh, entirely free from oil, acid, alkali, vegetable or organic matter, or any other deleterious substance in suspension or in solution or as sediment. - Cement-based mortar may incorporate additives conforming to BS EN 934 (or equivalent) and compatible with the other mortar constituents. The use of calcium chloride, or additives containing calcium chloride, is prohibited. - Cement-based mortar may incorporate lime to EN 459-1 (or equivalent). - Constituent materials may be batched by volume, using clean and accurate gauge boxes or buckets. The mix proportions shall be based on damp sand, with adjustments being made to the mix proportions to compensate for dry sand. Mixing of the mortar shall be carried out in a pan type, or a tilting-drum mixer, properly maintained and in a clean condition. - Pre-mixed (factory-made) cement-based renderings shall consist of mortar containing Portland cement and sand, in agreed proportions, to the external or internal surface of the building, in one or more layers. - Pre-mixed cement-based renderings shall conform to EN 998-1(or equivalent). |  |  |
|  | Internal Pre-Mixed (Factory Made) Cement-Based Rendering Mortar |  |  |
|  | - Cement-based mortar for internal use shall consist of one base coat and one plain finishing coat, with an overall thickness 6mm on walls and ceilings, exclusive of keying depths and dubbing coats. If metal lathing is used, this overall thickness shall be achieved from the surface of the metal lathing. - The nominal size of the finishing coat plaster shall be less than 0.6mm. |  |  |
|  | External Pre-Mixed (Factory Made) Cement-Based Rendering Mortar |  |  |
|  | - Cement-based mortar for external use shall consist of one base coat and one plain finishing coat, with an overall thickness 9mm on walls and ceilings, exclusive of keying depths and dubbing coats. If metal lathing is used, this overall thickness shall be achieved from the surface of the metal lathing. - The nominal size of the finishing coat plaster shall be less than 0.6mm. |  |  |
|  | Internal Pre-Mixed Gypsum Plastering |  |  |
|  | - Internal plastering shall conform to the recommendations of BS 5492: 1990 (or equivalent), Code of Practice for Internal Plastering. - The gypsum-based mortar shall be applied to internal wall surfaces in two layers, namely a base coat and a finishing coat. - The base coat shall consist of a 6mm pre-mixed plaster based on gypsum, hydraulic lime and additional materials such as expanded perlite and additives to assist fluidity control, support adherence, setting and working times. - Smooth concrete and dusty surfaces shall be treated with an appropriate adhesion primer, consisting of organic resins in a water-based emulsion. - The base coat plaster shall be applied initially as a thin coat firmly worked into the substrate, and then gradually brought to full specification thickness. The coat shall be brought to a level surface using a metal straight edge, and shall then be cross-scratched to form a mechanical key. - Base coats on adjacent dissimilar materials shall be assisted by isolation layers and metal lathing, as specified above, and by plastering on metal lathing, after ensuring that the lathing is taut and fixed with key facing outwards. - Tying wire ends shall be bent inwards, and any cut edges, staples or nail heads shall be painted with bitumen to avoid rust staining. - Plasters shall be mixed in a paddle-type mixer, with machines and containers cleaned frequently, at least after every batch mix of gypsum plaster, and whenever different materials are used. Gypsum plasters shall not be used if initial set occurs before application. - The finishing coat for gypsum plastering shall be 3mm thick and shall be laid with a trowel, so as to achieve a tight matte smooth surface with no hollows, abrupt changes of level or trowel marks. - Rapid, premature or uneven drying out of the final coat shall not be allowed. - The finishing coat gypsum shall consist of gypsum, hydrated lime, rock powder and special adhesives and additives to increase workability and adhesion. - The finishing coat shall be applied using a stainless steel rectangular trowel, over the whole surface. The trowel shall have specially ground edges, and shall be made from extra-hard stainless and abrasion-proof steel. - The finished surfaces shall be even and consistent and free from rippling, hollows, ridges, cracks and crazing. - The finished surface shall be to a true plane, to the correct line and level, with angles and corners to the right angle, unless specified otherwise, and with walls and reveals plumb and square. - Surface flatness/regularity shall be acceptable if the deviation of the surface from a 1.8m straightedge does not exceed 3mm. |  |  |
|  | ### DESIGN & BUILD STRUCTURE |  |  |
|  | Scope of Works |  |  |
|  | - The Contractor shall be responsible for the complete design, engineering, fabrication, supply, delivery, installation, testing, certification and commissioning of an enclosed pedestrian bridge structure in accordance with the approved drawings, statutory requirements, and the provisions of this specification. - The Contractor shall submit detailed structural calculations, shop drawings, fabrication drawings and material specifications, duly endorsed by a warranted Structural Engineer, for approval prior to commencement of fabrication. - The completed structure shall be delivered fully operational, weatherproof, safe, durable, and fit for its intended purpose. |  |  |
|  | General Requirements |  |  |
|  | - The enclosed structure shall consist of a lightweight, corrosion-resistant structural system designed to withstand all applicable dead, live, wind and environmental loads in accordance with current Eurocodes and Maltese Building Regulations. - The design shall take into consideration the marine environment and shall incorporate suitable materials and protective treatments to ensure long-term durability and minimal maintenance requirements. - All materials and workmanship shall be of premium quality and shall comply with the latest applicable European Standards. |  |  |
|  | Structural Frame |  |  |
|  | - The primary structural framework shall consist of premium-grade architectural aluminium sections specifically designed for structural glazing applications. - The aluminium system shall: - Be extruded from high-grade aluminium alloy suitable for structural applications. - Be designed to accommodate thermal movement, wind loads and glazing loads. - Incorporate concealed drainage and fixing systems wherever practicable. - Include all necessary brackets, stiffeners, connectors, anchors and fixing components. - Be powder-coated to an approved colour and finish, suitable for external exposure and marine environments. - The Contractor shall be solely responsible for verifying structural adequacy and detailing all connections to the existing building structure. |  |  |
|  | Glazing Enclosure |  |  |
|  | - The side walls and roof enclosure shall be constructed using high-performance double-glazed panels. - The glazing system shall: - Consist of safety double-glazing throughout. - Comply with applicable European Standards for impact resistance and human safety. - Provide adequate thermal and acoustic performance. - Be securely fixed within the aluminium framing system using proprietary gaskets and fixing arrangements. - Be fully weatherproof and watertight. - Include all sealants, flashings and weatherproofing details necessary to prevent water ingress. - The roof glazing shall be designed to safely withstand maintenance loads and all applicable imposed loads. |  |  |
|  | Floor Ramp |  |  |
|  | - The enclosed bridge shall incorporate a continuous accessibility ramp extending between the designated levels shown on the approved drawings. - The ramp shall: - Be designed and constructed with a maximum gradient of 1:12. - Comply fully with the requirements of the Commission for the Rights of Persons with Disability (CRPD). - Be finished flush with adjoining floor levels at both ends to provide a seamless transition. - Be free from trip hazards, abrupt level changes or discontinuities. - Be designed to safely accommodate pedestrian traffic and maintenance loads. - Incorporate a durable, slip-resistant floor finish suitable for both wet and dry conditions. - The Contractor shall ensure that all dimensions, gradients, landings and clear widths comply with the latest accessibility requirements and the approved permit. |  |  |
|  | Safety Railings |  |  |
|  | - Safety railings shall be provided throughout the length of the bridge and ramp. - The railing system shall: - Be designed, supplied and installed in full compliance with MSA 3500:2010 or its latest revision. - Incorporate smooth and continuous surfaces free from sharp edges or projections. - Be fabricated from same aluminium as rest of the structure - Be securely fixed and detailed to prevent loosening during service. |  |  |
|  | Grab Rails |  |  |
|  | - Continuous grab rails shall be provided on both sides of the ramp and bridge structure. - The grab rail system shall: - Comply with the Access for All Design Guidelines 2011, or the latest edition issued by the Commission for the Rights of Persons with Disability (CRPD). - Be continuous for the full accessible route. - Include extensions, returns and clearances as required by the applicable guidelines. - Be positioned at compliant heights and offsets. - Provide a comfortable and secure grip surface. - Be fabricated from durable corrosion-resistant materials suitable for public use. |  |  |
|  | Finishes |  |  |
|  | - All exposed components shall be finished to a premium architectural standard. - The scope shall include: - Powder-coated aluminium finishes. - Finished exposed fixings and trims. - Silicone and sealant works. - Flashings and weatherproofing components. - Colour of aluminium to be approved by the Architect in Charge prior to order |  |  |
|  | Design Responsibility |  |  |
|  | - The Contractor shall assume full design responsibility for the completed structure and shall ensure compliance with: - Approved architectural drawings. - Eurocodes and associated National Annexes. - Maltese Building Regulations. - MSA 3500:2010. - Access for All Design Guidelines issued by CRPD. - Occupational Health and Safety requirements. - Any other statutory requirements applicable at the time of execution. - All calculations and drawings shall be prepared and endorsed by the contractor’s Warranted Perit key expert, to be approved by the Architect in Charge. Prior to order, the contractor shall provide the AIC with design drawings and upon review, revisions and approval, shop drawings shall be prepared (by the contractor). Fabrication shall only start upon the AIC’s approval of the shop drawings. |  |  |
|  | Completion and Certification |  |  |
|  | - Upon completion, the Contractor shall provide: - Certification to be issued by the contractor’s Warranted Perit Key Expert. - Material warranties. - Glazing compliance certificates. - As-built drawings. - The works shall be deemed complete only upon successful inspection, testing, certification and approval by the Architect in Charge and the relevant authorities, including CRPD. |  |  |
|  | ### SANITARY FACILITIES |  |  |
|  | Green Public Procurement |  |  |
|  | Toilets |  |  |
|  | Flushing Toilet Equipment |  |  |
|  | Full flush volume The nominal full flush volume, independent of the water pressure, of flushing toilet equipment when placed on the market shall not exceed 6.0 l/flush. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, test results according to the test procedure contained in standard EN 997 or equivalent standards shall be submitted. The testing shall be performed by laboratories that meet the general requirements of standard EN ISO 17025 or equivalent. |  |
|  | Flushing system requirements Flushing systems shall comply with the requirements of the respective EN standards listed in Table 1. Table 1. EN standards on toilet flushing system requirements: Number; Title. EN 14055; WC and urinal flushing cisterns. EN 12541; Sanitary tapware - Pressure flushing valves and automatic closing urinal valves PN10. EN 15091; Sanitary tapware - Electronic opening and closing sanitary tapware. |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, a test report showing that the flushing system of the product complies with the requirements of the respective EN standards mentioned above or equivalent standards will be accepted. |  |
|  | Flushing Performance The flush performance of toilet suites and toilet receptacles shall comply with the requirements of standard EN 997. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, a test report showing that the flush performance of the product complies with the requirements of Standard EN 997 or equivalent standard will be accepted. |  |
|  | Installation instructions / user information The toilet flushing equipment shall be supplied with the following information in print (on the packaging and/or on documentation accompanying the product) and/or electronic format: – Proper installation instructions, including information on which class(es) and/or type(s) the product has been tested for, information on the specific operating pressures that the product is suitable for, information on which drainage system types the product can work with, information describing how to adjust the flush volumes as well as the consequences (e.g. in terms of residual water level, filling level, etc.) and, in the case of toilet receptacles and toilet flushing systems placed on the market independently, information on which products they shall be combined with to make a full functioning unit that is water efficient; – Advice on how rational use can minimise the environmental impact, in particular information on proper product’s use to minimise consumption of water; – Information on full and reduced flush volumes in l/flush; – Recommendations on the proper use and maintenance of the product, including information on which spare parts can be replaced, instruction concerning replacement of washers and other fittings if the product leaks, cleaning advice, etc.; – Information concerning appropriate disposal at product’s end-of-life. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Other appropriate means of proof will also be accepted, such as written evidence from the manufacturer that the above clause will be met. |  |
|  | Sanitary Tapware |  |  |
|  | Maximum available water flow rate The maximum available water flow rates to the basin/sink shall, independent of the water pressure, not exceed values presented in Table 1. Table 1 Maximum available water flow rates for sanitary tapware Product sub-group; Water flow (l/ min). Kitchen taps; 8.0. Basin taps; 7.0. Showerheads or showers[1]; 9.0. Note [1]: Showerheads or showers with more than one spray pattern shall fulfil the requirement for the setting with the highest water flow. |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, results of sanitary tapware testing according to the test procedure contained in the relevant EN standard (see the list in Table 2 below) or an equivalent standard shall be submitted together with the tender to the contracting authority. The testing shall be conducted at pressure of 1.5, 3.0 and 4.5 bar (± 0.2 bar) for products declared by the manufacturer as being suitable for high pressure installations (typically 1.0 to 5.0 bar) or at pressure of 0.2, 0.3 and 0.5 bar (± 0.02 bar) for products declared by the manufacture as being suitable for low pressure installations (typically 0.1 to 0.5 bar). The mean value of the three measurements shall not exceed the maximum water flow rate value indicated in Table 1. The testing shall be performed by laboratories that meet the general requirements of EN ISO 17025 or equivalent. A technical dossier from the manufacturer or other appropriate means of proof demonstrating that these requirements have been met will also be accepted. Table 2 EN standards for sanitary tapware; Number; Title. EN 200; Sanitary tapware. Single taps and combination of taps for water supply systems of type 1 and type 2 - General technical specification. EN 816; Sanitary tapware. Automatic shut-off valves (PN10). EN 817; Sanitary tapware. Mechanical mixing valves (PN10) - General technical specifications. EN 1111; Sanitary tapware. Automatic shut-off valves (PN10). EN 1112; Sanitary tapware. Shower outlets for sanitary tapware for water supply systems type 1 and type 2 - General technical specification. EN 1286; Sanitary tapware. Low pressure mechanical mixing valves. General technical specification. EN 1287; Sanitary tapware. Low pressure termostatic mixing valves. General technical specification. EN 15091; Sanitary tapware. Electronic opening and closing sanitary tapware .. EN 248; Sanitary tapware. General specification for electrodeposited coatings of Ni-Cr. EN60335-1; Household and Similar Electrical Appliances. EN60335-2-35; Household and Similar Electrical Appliances, Safety, Particular Requirements for Instantaneous Water heaters. |
|  | Lowest maximum available water flow rate Lowest maximum available water flow rate of the sanitary tapware, independent on the water pressure, shall not be lower that the values given in Table 3: Table 3 Lowest maximum available water flow rates for sanitary tapware Product sub-group; Water flow (l/ min). Kitchen taps; 2.0. Basin taps; 2.0. Showerheads or showers; 4.5. Electric shower and low pressure shower2; 3.0. Note [1]: Showerheads or showers with more than one spray pattern shall fulfil the requirement for the setting with the highest water flow. |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, result of sanitary tapware testing according to the test procedure contained in the relevant EN standard (see the list in Table 2) or an equivalent standard shall be submitted together with the tender to the contracting authority for verification. The testing shall be conducted at pressure of 1.5, 3.0 and 4.5 bar (± 0.2 bar) for products declared by the manufacture as being suitable for high pressure installations (typically 1.0 to 5.0 bar) or at pressure of 0.2, 0.3 and 0.5 bar (± 0.02 bar) for products declared by the manufacture as being suitable for low pressure installations (typically 0.1 to 0.5 bar). The mean value of the three measurements shall not be lower than the water flow rate value indicated in Table 3. The testing shall be performed by laboratories that meet the general requirements of EN ISO 17025 or equivalent. A technical dossier from the manufacturer or other appropriate means of proof demonstrating that these requirements have been met will also be accepted. |  |
|  | Temperature management (criterion not applicable for showerheads and for sanitary tapware that shall be fitted to a water supply that is already temperature controlled) Sanitary tapware shall be equipped with an advanced device or technical solution which allows for management of temperature. According to their preferences, public authorities can choose one of the following options: a) Sanitary tapware shall be equipped with a hot water barrier. b) Sanitary tapware shall allow for thermostatic adjustment. c) Sanitary tapware shall be designed with a cold water supply in middle position. Double lever/handle showers do not fulfil the criterion. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Other appropriate means of proof will also be accepted, e.g. manufacturer/supplier statement specifying the type of solution used and its technical parameters, as appropriate, shall be submitted. Where a water supply is already temperature controlled the tenderer shall explain the specific technical property that makes the sanitary tapware specifically designed to be fitted to this form of system. |  |
|  | Time control for sanitary tapware for multiple users and high frequency use Sanitary tapware installed in non-domestic premises for multiple users and for frequent use (i.e. sanitary tapware used in public toilets or washrooms in schools, offices, in hospitals, swimming-pools and similar premises) shall allow for limiting time of a single water use (i.e. water volume consumed). This can be done by equipping the products with devices which stop water flow after certain time if they are not used (for example, sensors which stop water flow when a user leaves the sensor range) and/or after a set time period of use (for example, time limiters, which stop the water flow when the maximum flow time is reached). a) If the public authority is wishing to have a time-controlled system: For sanitary tapware equipped with time limiters the pre-set maximum flow should not exceed 15 seconds for taps and 35 seconds for showers. Nevertheless, the product shall be designed to allow the installer to adjust the flow time to the intended product’s application. b) If the public authority is wishing to have a sensor-controlled system: For sanitary tapware equipped with the sensor, the shut off delay time after usage shall not exceed 2 second for taps and 3 seconds for showers. Furthermore, the sanitary tapware equipped with a sensor shall be equipped with an inbuilt ‘security technical feature’ with a pre-set shut-off time of maximum 2 minutes in order to prevent accidents or the continuous water flow from taps/showers when not in use. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Other appropriate means of proof will also be accepted, e.g. manufacturer/supplier statement specifying the type of solution used and its technical parameters, as appropriate, shall be submitted. Where a water supply is already temperature controlled the tenderer shall explain the specific technical property that makes the sanitary tapware specifically designed to be fitted to this form of system. |  |
|  | Exposed surface condition and quality of coating Sanitary products which have a metallic Ni-Cr coating (regardless of the nature of the substrate material) shall comply with the standard EN 248. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Otherwise, results of sanitary tapware testing according to the test procedure contained in the EN 248 standard or equivalent shall be submitted together with the tender to the contracting authority for verification. The testing shall be performed by laboratories that meet the general requirements of EN ISO 17025 or equivalent. A technical dossier from the manufacturer or other appropriate means of proof demonstrating that these requirements have been met will also be accepted. |  |
|  | Reparability and availability of spare parts The product shall be designed in such a way that its exchangeable components can be replaced easily by the enduser or a professional service engineer, as appropriate. Information about which elements can be replaced shall be clearly indicated in the information sheet attached to the product. The tenderer shall also provide clear instructions to enable the end-user or trained experts, as appropriate, to undertake basic repairs. The tenderer shall further ensure that spare parts are available for at least five years from the date of purchase. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Other appropriate means of proof will also be accepted such as written evidence from the manufacturer that the above clause is met. The tenderer shall provide a description of how to replace components and provide a guarantee for the availability of spare parts. |  |
|  | User information The product shall be supplied with the following information in printed (on the packaging and/or on documentation accompanying the product) and/or electronic format: (a) installation instructions, including information on the specific operating pressures that the product is suitable for, (b) recommendations on the proper use and maintenance (including cleaning and decalcification) of the product, mentioning all relevant instructions, particularly: (i) advice on maintenance and use of products, (ii) information about which spare parts can be replaced, (iii) instructions concerning the replacement of washers if taps drip water, (iv) advice on cleaning sanitary tapware with appropriate materials in order to prevent damage to their surfaces, (v) advice on regular and proper service of aerators. |  |  |
|  | Verification: | Products holding a relevant Type 1 Eco-label fulfilling the listed requirements will be deemed to comply. Other appropriate means of proof will also be accepted such as written evidence from the manufacturer that the above clause is met |  |

SECTION 5 – SUPPLEMENTARY DOCUMENTATION

## 5.1 – Draft Contract Form

## 5.2 – Glossary

## 5.3 – Specimen Performance Guarantee

## 5.4 – Specimen Tender Guarantee

## 5.4 – General Conditions of Contract

The full set of General Conditions for Works Contracts (latest version as applicable on the date of the publication of this tender) can be viewed/downloaded from the ‘Resources Section’ at:

www.etenders.gov.mt

It is hereby construed that the tenderers have availed themselves of these general conditions, and have read and accepted in full and without reservation the conditions outlined therein, and are therefore waiving any standard terms and conditions which they may have.

These general conditions will form an integral part of the contract that will be signed with the successful tenderer/s.

## 4.8 – General Rules Governing Tendering for NGOs

The contents of this procurement document complement the latest version of the General Rules Governing Tenders applicable on the date of the publication of this tender, the Terms of Use and the Manual for Economic Operators applicable to Government’s e-Procurement Platform (available from the Resources section of www.etenders.gov.mt).